## Notes
Notes.
1. | This sheet ihas been made for the design of foundation with piles.
2. | Analysis has done by STAAD.Pro 2003.
3. | For stability check and design, the load combinations used, are same for pipe rack and structure because these are almost same in actulal as per specs.
4. | For stability check, pile reactions have been taken for 701 to 830 load cases of STAAD.
5. | For foundation design, pile reactions have been taken for 101 to 234 of STAAD.
6. | For foundation design there has made two groups of plates in STAAD.Pro 2003.
One group is named as "Moment" having selected plates not including plates under pedestal.(Because critical; section for moment is at the face of pedestal.)
For flexure reinforcement design, we have used this group to take out the design moment.
Other group is named as "Shear" having selected plates only at a distance 'd' from the face of pedestal.
For wide beam shear strength, we have used this group to take out the applied shear values.
7. | For punching shear basically the maximum pedestal force has been taken to calculate force causing punching shear.
This can be done in STAAD using maximum beam results in post processing mode.

## Eqpt Foundation Design
VIETNAM OIL AND GAS CORPORATION ( PETROVIETNAM )
DUNG QUAT REFINERY (DQR) PROJECT
4.1- COMPUTER MODEL
A "plate on elastic foundation" model is set up in STAAD-Pro. The piles are modeled as springs having same end properties like pile,
pin connected with foundation. All the forces resulting from the structure weights are calculated as per given information and applied
on the top of pedestal.
3D RENDERED VIEW FOR FOUNDATION
STAAD Global Axis | [8 empty] | STAAD Plate Local Axis
General
| - | Item No. | H-1503-F2
| - | Service | EQUIPMENT FOUNDATION
| - | Type
Document
| - | Refer to Dwg.No.
Elevation
| - | Top of Foundation Elev. |  | EL + | 98.5 | (m)
| - | Unit Elevation |  | GL=+ | 100 | (m) | (HPP EL)
| - | Ground water table |  | GWL - |  | (m)
| - | Top of Pedestal Elev. |  | EL + | SEE DWG. | (m)
Foundation Geometry
|  |  |  | Length (X-Dir.) | 6.5 | (m)
|  |  |  | Width (Y-Dir.) | 4.5 | (m)
|  |  |  | Thickness | 0.7 | (m)
|  |  |  | Pedestal Length. | 0.6 | (m)
|  |  |  | Pedestal Width | 0.6 | (m)
|  |  |  | Pedestal Ht. | SEE DWG. | (m)
|  |  |  | Span b/w Pedestals | SEE DWG. | (m)
|  |  |  | Ht. From Eq. C.L to Pedestal Top | SEE DWG. | (m)
Node Numbers
Plate Numbers
4.2- LOADING DATA
LOADING AT PEDESTAL TOP
PEDESTAL AT NODE # 81 |  |  |  | Vertical | Horizontal |  | Moment
|  |  |  | Fy | X-dir. | Z-dir. | X-dir. | Z-dir.
|  |  |  | kN | kN | kN | kN-m | kN-m
Equipment Load for Erection |  |  | : EQE | -550
Equipment Load for Operation |  |  | : EQO
Equipment Load for Test |  |  | : EQT1
Live Load |  |  | : LL
Equipment Wind Load +X |  |  | : WX | 40 | -20
Equipment Wind Load +Z |  |  | : WZ | -80 |  | 40
Seismic Load +X |  |  | : EX | 230 | -115
Seismic Load +Z |  |  | : EZ | -230 |  | 120
Thermal Force |  |  | : THX | 20 | -10
Thermal Force |  |  | : THZ
PEDESTAL AT NODE # 82 |  |  |  | Vertical | Horizontal |  | Moment
|  |  |  | Fy | X-dir. | Z-dir. | X-dir. | Z-dir.
|  |  |  | kN | kN | kN | kN-m | kN-m
Equipment Load for Erection |  |  | : EQE | -450
Equipment Load for Operation |  |  | : EQO
Equipment Load for Test |  |  | : EQT1
Live Load |  |  | : LL
Equipment Wind Load +X |  |  | : WX | -10 | -10
Equipment Wind Load +Z |  |  | : WZ | -120 |  | 50
Seismic Load +X |  |  | : EX | -200 | -130
Seismic Load +Z |  |  | : EZ | -425 |  | 125
Thermal Force |  |  | : THX | -10 | -10
Thermal Force |  |  | : THZ
PEDESTAL AT NODE # 83 |  |  |  | Vertical | Horizontal |  | Moment
|  |  |  | Fy | X-dir. | Z-dir. | X-dir. | Z-dir.
|  |  |  | kN | kN | kN | kN-m | kN-m
Equipment Load for Erection |  |  | : EQE | -550
Equipment Load for Operation |  |  | : EQO
Equipment Load for Test |  |  | : EQT1
Live Load |  |  | : LL
Equipment Wind Load +X |  |  | : WX | 40 | -20
Equipment Wind Load +Z |  |  | : WZ | 80 |  | 40
Seismic Load +X |  |  | : EX | 230 | -115
Seismic Load +Z |  |  | : EZ | 230 |  | 120
Thermal Force |  |  | : THX | 20 | -10
Thermal Force |  |  | : THZ
PEDESTAL AT NODE # 84 |  |  |  | Vertical | Horizontal |  | Moment
|  |  |  | Fy | X-dir. | Z-dir. | X-dir. | Z-dir.
|  |  |  | kN | kN | kN | kN-m | kN-m
Equipment Load for Erection |  |  | : EQE | -450
Equipment Load for Operation |  |  | : EQO
Equipment Load for Test |  |  | : EQT1
Live Load |  |  | : LL
Equipment Wind Load +X |  |  | : WX | -10 | -10
Equipment Wind Load +Z |  |  | : WZ | 120 |  | 50
Seismic Load +X |  |  | : EX | -200 | -130
Seismic Load +Z |  |  | : EZ | 425 |  | 125
Thermal Force |  |  | : THX | -10 | -10
Thermal Force |  |  | : THZ
4.3- LOADING DIAGRAMS
4.3.1- SELF WEIGHT OF FOUNDATION (KN):-
The self weight of foundation has been calculated by STAAD itself as per material and geometric properties given to the STAAD.
4.3.2- SOIL WT & PEDESTAL WEIGHT. (kN/m2)
4.3.3- EQUIPMENT EMPTY LOAD (kN)
4.3.7- WIND LOAD X-DIRECTION (kN)
4.3.8- WIND LOAD Z-DIRECTION (kN, kN-m)
4.3.9- SEISMIC LOAD X-DIRECTION (kN)
4.3.10- SEISMIC LOAD Z-DIRECTION (kN, kN-m)
4.3.11- THERMAL SLIDING FORCE-X (kN)
4.3.11- THERMAL SLIDING FORCE-Z (kN)
4.4- DETERMINATION OF SOIL SPRING
The piles are modeled as springs in the STAAD model for the above foundation. The properties for spring are the same as that for for a pile connected
with foundation as a pin ie only vertical and lateral forces can be resisted by pile. No of piles are tried to reduce as minimum as possible keeping in mind the
geomatricaly balance force distribution on piles.
4.5- STABILITY CHECKS
Pile Reactions. (from 4.7)
| L/C | NODE NO. | Vert. Compr. | Vert.Tension | Horizontal Load |  | Type
| - | - | kN | kN | Hx (kN) | Hz (kN)
1 | 763 | 87 | 1371.276 |  |  |  | Short term
2 | 771 | 94 |  | 293.053 |  |  | Short term
3 | 759 | 94 |  |  | 95.776 |  | Short term
3 | [6 empty] | Short term
3 | [6 empty] | Short term
4 | 765 | 87 |  |  |  | 103.835 | Short term
Pile Bearing Capacity
|  | Pile Diameter |  |  |  |  | 0.8 | m
|  | V (long term) |  |  |  |  | 1700 | KN
|  | (short term) |  |  |  |  | 2261 | KN
|  | H |  |  |  |  | 146 | KN
|  | Uplift |  |  |  |  | -225 | KN
|  | No of Piles |  |  |  |  | 4
|  | Center of pile to edge spacing |  |  |  |  | see Dwg. | m
Lateral load capacity
Shear Capacity of
|  | Max Horizontal force on pile |  |  |  | Pile (kN)
|  | 95.776 |  |  |  | 194.6667 | OK !
NO !
NO !
NO !
NO !
NO !
NO !
NO !
NO !
NO !
NO !
NO !
NO !
NO !
NO !
NO !
Compression Capacity Check
|  | Max Compression |  |  |  | Pile Capacity in
Compression (kN)
|  | 1371.276 |  |  |  | 2261 | OK !
NO !
NO !
NO !
NO !
NO !
NO !
NO !
|  |  |  | #REF! |  |  | #REF!
NO !
NO !
NO !
NO !
NO !
NO !
NO !
Check Tension Force on Each Pile
|  | Max Tension |  |  |  | Pile Capacity in
Tension (kN)
|  | 293.053 |  |  |  | -225 | OK!
4.6- REINFORCMENT DESIGN OF MAT FOUNDATION
Reinforcement design has been done for the load combinations as mentioned in project spesification no. 8474L-000-JSD-1700-001
(Civil and Structural Design Criteria) clause 7.10(a). The list and designations of these combinations used in STAAD.Pro 2003 are from 101 to 234. Reinforcement
calculation has been performed for these load combinations.
4.6.1- Flexure Reinforcement
A- Plate Maximum Moment Results (kN-m)
Note. Results are taken as per STAAD plate local axis.
[5 empty] | X-Direction |  | Y-Direction
|  |  | Plate | L/C | Bottom | Top | Bottom | Top
|  |  | 69 | 164 LCC3 | -303.494
|  |  | 69 | 173 LCC3 |  | 216.361
|  |  | 102 | 167 LCC3 |  |  | -383.5
|  |  | 94 | 168 LCC3 |  |  |  | 344.436
B- Reinforcement Calculation
The reinforcement design is carried out as per the maximum design moment coming at the face of pedestal in both directions of foundation.
The reinforcement has been determined for 1 meter by 1 meter section as per design results of the STAAD for plate foundation.
| fy | 420 | N/mm2 |  | bX-Dir. | = | 1000 | (mm)
| fc' | 25 | N/mm2 |  | bY-Dir. | = | 1000 | (mm)
| Cover Bottom | 50 | mm |  | h | = | 700 | (mm)
| Cover Top | 50 | mm
Limits for Re-bar ratio are
| Minimum p1 = 0.0018*( h/d ) |  |  |  |  | Ref: | (ACI 318 Sec. 7.12.2)
| Minimum p1-1 = 4/3 * pr | [5 empty] | (ACI 318 Sec. 10.5.3)
| Minimum p1-2 = 1.4 / fy |  |  | = | 0.0033333 |  | (ACI 318 Sec. 10.5.1)
| Maximum p2 |  |  | = | 0.018973 |  | (ACI 318 Sec. 10.3.3)
C- Reinforcement Calculation
|  |  |  | X-Direction |  | Y-Direction
|  |  | Bar Size | Bottom | Top | Bottom | Top
|  |  |  | 25 | 25 | 25 | 25
|  |  | No. of bars | 5.36 | 5.36 | 5.36 | 5.36
|  |  | Pitch | 200 | 200 | 200 | 200
|  |  | d | 612.5 | 612.5 | 637.5 | 637.5
|  |  | b | 1000 | 1000 | 1000 | 1000
|  |  | Rn | 0.89887 | 0.6408 | 1.0485 | 0.94168
|  |  | preq. | 0.0021874 | 0.0015494 | 0.0025612 | 0.0022941
|  |  | Min. p1 | 0.0010286 | 0.0010286 | 0.00098824 | 0.00098824
|  |  | Min. p1-1 | 0.0029166 | 0.0020659 | 0.003415 | 0.0030588
|  |  | pDesign. | 0.0029166 | 0.0020659 | 0.0033333 | 0.0030588
|  |  | AsProv. | 2631.0838 | 2631.0838 | 2631.0838 | 2631.0838
|  |  | AsDesign. | 1786.414 | 1265.3808 | 2125 | 1950.0001
|  |  | Judge | O.K | O.K | O.K | O.K
D- Reinforcement to be Provided
|  |  |  | X-Direction |  | Y-Direction
|  |  | No. | Bottom | Top | Bottom | Top
|  |  |  | 5.36-D25@200 | 5.36-D25@200 | 5.36-D25@200 | 5.36-D25@200
4.6.2- Check for Shear Strength
A- Check of Shear Strength for Two-way Action (Punching shear)
Note. Results are taken as per STAAD global axis.
|  |  |  | Nmax | Node | L/C | R
|  |  |  | (kN) | - | - | (kN)
|  |  | Max Fy | 1136.703 | 90 | 167 LCC3 | 1820.099
Nmax = Max. factored vertical force on column
| R =Soil Reaction at Column location |  |  | wx = | 6.5 | m | wx1 = | 3.25 | m
| bo = 2(px+d)+2(py+d) |  |  | wy = | 4.5 | m | wx2 = | 3.25 | m
| bc = Max pxy / Min pxy | [5 empty] | wy1 = | 2.25 | m
| bo/d | [5 empty] | wy2 = | 2.25 | m
| @ = alpha | = | 20 | d = | 0.6125 | m
| Vc1 = 0.75*(2+4/bc)*f'c^0.5*bod |  | : (kips) | ACI 318 11.12.2.1 EQU(11-35)
| Vc2 = 0.75*(@d/bo+2)*f'c^0.5*bod |  | : (kips) | ACI 318 11.12.2.1 EQU(11-36)
| Vc3 = 0.75*4*f'c^0.5bod |  | : (kips) | ACI 318 11.12.2.1 EQU(11-37)
Vpu < min ( Vc1 , Vc2 , Vc3 )
|  |  |  | px | py | Lpx | Lpy |  |  |  | fc = | 3628.3163 | psi
|  |  |  | m | m | m | m
|  |  | No.1 | 0.6 | 0.6
| Nmax | px+d | py+d | Vpu | bo | bc | Vc1 | Vc2 | Vc3 | Judge
| kN | m | m | kN | mm |  | kN | kN | kN
No.1 | 1136.703 | 1.2125 | 1.2125 | 683.396 | 4850 | 1.2 | 4931.571 | 4184.8448 | 3698.6783 | OK
B -Check of Shear Strength for One-way Action
|  |  |  | SQX | SQY | Plate No. | L/C
|  |  |  | (N/mm2) | (N/mm2) | - | -
|  |  | Max SQX | 0.471 |  | 68 | 166 LCC3
|  |  | Min SQX | -0.457 |  | 68 | 163 LCC3
|  |  | Max SQY |  | 0.402 | 65 | 168 LCC3
|  |  | Min SQY |  | -0.402 | 68 | 170 LCC3
X-Direction
Max. SQX = | 0.471 | N/mm2
Vc/bd = 0.75*0.17f'c^0.5 |  | = | 0.62293 | N/mm2 > | 0.471 | O.K
Y-Direction
Max. SQY = | 0.402 | N/mm2
Vc/bd = 0.75*0.17f'c^0.5 |  | = | 0.62293 | N/mm2 > | 0.402 | O.K
4.6- DESIGN OF PEDESTAL
Design of pedestal has been carried out by STAAD as a column in the foundation model. The results are shown for the selected pedestals as
given below in the diagram. The same reinforcement is provided in the drawing.
Z
X
Y
Y
X
Z
83
84
82
81
-27.0

## Pile Reactions
Support Reactions for Load Comb. 701~830
| A | Horizontal | Horizontal | Vertical | Horizontal | Moment | G | H
| Node | L/C | Fx kN | Fy kN | Fz kN | Mx kNm | My kNm | Mz kNm
Max Fx | 94 | 759 | 95.776 | 628.757 | -6.595 | 0 | 0.727 | 0
Min Fx | 90 | 761 | -95.776 | 1114.84 | -6.595 | 0 | 0.727 | 0
Max Fy | 87 | 763 | 6.275 | 1371.276 | -103.796 | 0 | -0.048 | 0
Min Fy | 94 | 771 | 6.837 | 293.053 | -95.116 | 0 | 0.046 | 0
Max Fz | 87 | 765 | 3.744 | 544.044 | 103.835 | 0 | -0.031 | 0
Min Fz | 91 | 763 | 3.744 | 544.078 | -103.835 | 0 | 0.031 | 0
Max Mx | 87 | 701 | 18.195 | 968.031 | 0.119 | 0 | -0.144 | 0
Min Mx | 87 | 701 | 18.195 | 968.031 | 0.119 | 0 | -0.144 | 0
Max My | 94 | 759 | 95.776 | 628.757 | -6.595 | 0 | 0.727 | 0
Min My | 90 | 760 | 95.776 | 628.756 | 6.595 | 0 | -0.727 | 0
Max Mz | 87 | 701 | 18.195 | 968.031 | 0.119 | 0 | -0.144 | 0
Min Mz | 87 | 701 | 18.195 | 968.031 | 0.119 | 0 | -0.144 | 0

## Design Shear Values
Design Shear for Load Comb. 101~234
| A | Shear | Shear | Membrane | Membrane | F | Bending Moment | Bending Moment | I | J
| Plate | L/C | SQX N/mm2 | SQY N/mm2 | SX N/mm2 | SY N/mm2 | SXY N/mm2 | Mx kNm/m | My kNm/m | Mxy kNm/m
Max Qx | 68 | 166 LCC3 | 0.471 | -0.044 | 0.004 | 0 | -0.006 | -54.868 | 1.405 | -1.477
Min Qx | 68 | 163 LCC3 | -0.457 | 0.043 | -0.004 | 0 | 0.006 | -73.814 | -29.658 | 1.582
Max Qy | 65 | 168 LCC3 | 0.018 | 0.402 | 0.015 | 0.01 | 0.001 | -87.746 | 107.6 | 4.505
Min Qy | 68 | 170 LCC3 | 0.018 | -0.402 | 0.015 | 0.01 | -0.001 | -87.746 | 107.6 | -4.505
Max Sx | 70 | 170 LCC3 | -0.102 | 0.04 | 0.03 | -0.005 | 0.006 | -98.931 | -11.489 | -9.691
Min Sx | 70 | 167 LCC3 | -0.158 | -0.047 | -0.03 | 0.005 | -0.006 | 19.24 | 9.872 | 1.412
Max Sy | 81 | 165 LCC3 | -0.196 | 0.118 | -0.01 | 0.027 | 0.001 | 125.265 | 5.707 | 3.372
Min Sy | 81 | 164 LCC3 | 0.212 | -0.028 | 0.01 | -0.027 | -0.001 | -106.806 | 3.599 | -2.373
Max Sxy | 99 | 169 LCC3 | -0.023 | 0.313 | 0.003 | 0.005 | 0.017 | 18.475 | 21.645 | 32.205
Min Sxy | 95 | 167 LCC3 | -0.023 | -0.313 | 0.003 | 0.005 | -0.017 | 18.475 | 21.645 | -32.205
Max Mx | 81 | 165 LCC3 | -0.196 | 0.118 | -0.01 | 0.027 | 0.001 | 125.265 | 5.707 | 3.372
Min Mx | 72 | 164 LCC3 | 0.122 | 0.092 | 0.012 | 0.006 | -0.004 | -130.251 | -8.17 | -2.393
Max My | 26 | 168 LCC3 | 0.147 | -0.149 | 0.001 | -0.012 | 0 | 14.374 | 159.792 | -16.143
Min My | 32 | 168 LCC3 | -0.047 | -0.085 | -0.001 | 0.012 | -0.002 | -4.565 | -219.959 | -2.423
Max Mxy | 17 | 168 LCC3 | -0.103 | 0.108 | 0 | -0.01 | -0.003 | 10.499 | 114.138 | 37.242
Min Mxy | 23 | 170 LCC3 | -0.103 | -0.108 | 0 | -0.01 | 0.003 | 10.499 | 114.138 | -37.242

## Design Moment Values
Design Moment for Load Comb. 101~234
| A | Shear | Shear | Membrane | Membrane | F | Bending Moment | Bending Moment | I | J
| Plate | L/C | SQX N/mm2 | SQY N/mm2 | SX N/mm2 | SY N/mm2 | SXY N/mm2 | Mx kNm/m | My kNm/m | Mxy kNm/m
Max Qx | 89 | 170 LCC3 | 2.57 | 0.087 | -0.002 | 0.005 | -0.142 | 2.823 | -124.854 | -203.567
Min Qx | 86 | 169 LCC3 | -2.626 | 0.159 | 0 | 0.004 | 0.155 | -0.062 | -151.985 | 218.283
Max Qy | 102 | 169 LCC3 | -0.838 | 1.25 | -0.006 | -0.003 | 0.139 | 96.486 | 342.441 | 185.469
Min Qy | 94 | 167 LCC3 | -0.838 | -1.25 | -0.006 | -0.003 | -0.139 | 96.486 | 342.441 | -185.469
Max Sx | 89 | 163 LCC3 | 0.638 | -0.306 | 0.179 | 0.037 | 0.002 | 153.032 | 29.192 | 116.641
Min Sx | 89 | 166 LCC3 | 1.805 | -0.401 | -0.179 | -0.037 | -0.002 | -66.301 | 51.174 | -162.451
Max Sy | 85 | 169 LCC3 | 0.262 | -0.899 | 0.007 | 0.07 | -0.022 | 80.129 | 101.364 | 60.726
Min Sy | 85 | 168 LCC3 | 0.394 | -0.194 | -0.007 | -0.07 | 0.022 | 67.219 | 9.869 | -65.085
Max Sxy | 86 | 170 LCC3 | -2.583 | 0.165 | 0.016 | 0.007 | 0.155 | 9.578 | -153.641 | 206.844
Min Sxy | 86 | 167 LCC3 | -0.157 | -0.839 | -0.016 | -0.007 | -0.155 | 65.917 | 225.741 | -152.864
Max Mx | 69 | 173 LCC3 | 0.707 | -0.361 | 0.018 | 0.016 | -0.026 | 216.361 | 68.939 | -84.157
Min Mx | 69 | 164 LCC3 | -0.604 | 0.657 | -0.018 | -0.017 | 0.026 | -303.494 | -76.851 | 96.494
Max My | 94 | 168 LCC3 | -0.8 | -1.242 | 0.001 | -0.001 | -0.139 | 107.541 | 344.436 | -193.167
Min My | 102 | 167 LCC3 | -1.081 | -0.545 | -0.001 | 0.001 | -0.139 | -65.991 | -383.5 | -156.981
Max Mxy | 86 | 169 LCC3 | -2.626 | 0.159 | 0 | 0.004 | 0.155 | -0.062 | -151.985 | 218.283
Min Mxy | 80 | 167 LCC3 | -2.626 | -0.159 | 0 | 0.004 | -0.155 | -0.062 | -151.985 | -218.283

## Maximum Beam Forces
Maximum Beam Forces for Load Case 101~234
| Beam | L/C | Node | Fx kN | Fy kN | Fz kN | Mx kNm | My kNm | Mz kNm
Max Fx | 76 | 167 LCC3 | 6 | 1136.703 | -132.826 | 6.315 | 0 | -28.419 | -597.715
Min Fx | 74 | 176 LCC3 | 84 | -65.5 | -129.913 | -4.994 | 0 | 0 | 0
Max Fy | 74 | 169 LCC3 | 8 | 1136.703 | 132.826 | 6.315 | 0 | -28.419 | 597.715
Min Fy | 76 | 167 LCC3 | 6 | 1136.703 | -132.826 | 6.315 | 0 | -28.419 | -597.715
Max Fz | 73 | 170 LCC3 | 7 | 1113.438 | 6.367 | 148.927 | 0 | -670.172 | 28.652
Min Fz | 75 | 168 LCC3 | 5 | 1113.438 | 6.367 | -148.927 | 0 | 670.172 | 28.652
Max Mx | 76 | 164 LCC3 | 6 | 911.704 | 6.255 | 138.795 | 0 | -624.576 | 28.149
Min Mx | 76 | 106 LCA3 | 6 | 208.3 | 0.026 | -130.548 | 0 | 587.466 | 0.118
Max My | 75 | 168 LCC3 | 5 | 1113.438 | 6.367 | -148.927 | 0 | 670.172 | 28.652
Min My | 73 | 170 LCC3 | 7 | 1113.438 | 6.367 | 148.927 | 0 | -670.172 | 28.652
Max Mz | 74 | 169 LCC3 | 8 | 1136.703 | 132.826 | 6.315 | 0 | -28.419 | 597.715
Min Mz | 76 | 167 LCC3 | 6 | 1136.703 | -132.826 | 6.315 | 0 | -28.419 | -597.715
Maximum Spring Reactions at relavant node
Node No. | 90
| A | Horizontal | Vertical | Horizontal | Moment | F | G
| L/C | Fx kN | Fy kN | Fz kN | Mx kNm | My kNm | Mz kNm
| 167 LCC3 | 3.514 | 1820.099 | -132.555 | 0 | -0.034 | 0