## Slide 1
<number>
Connections
and
Bracing Configurations

## Slide 2
<number>
Introduction
This presentation was developed as a teaching aid with the support of the American Institute of Steel Construction. Its objective is to provide technical background and information for connections and bracing configurations. The information provided is based on common design and construction practices for structures of twelve stories or less.
The AISC Digital Library case study presentations document the construction of a steel frame for an office building. The case study includes photographs that were taken throughout the construction of the structural steel frame including detailing, fabrication, and erection. Project data including plans, schedules, specifications and other details are also included. The case study presentations are available in the Learning Opportunities section at www.aisc.org.
This presentation goes a step further in detail in the areas of connections and bracing configurations. A more in-depth background is provided and details of common connections and bracing configurations are presented.
The information is presented with concerns of a construction manager or general contractor in mind.

## Slide 3
<number>
What Will You Gain From This Presentation?
General knowledge of structural steel
Knowledge of the types of steel frame connections defined in the American Institute of Steel Construction design specification
An understanding of different types of connections used in structural steel frames
Insight into the impacts of using certain connection types
Familiarity with common bracing systems used in structural steel frames

## Slide 4
<number>
Benefits of Structural Steel
Some benefits associated with use of structural steel for owners are:
Steel allows for reduced frame construction time and the ability to construct in all seasons
Steel makes large spans and bay sizes possible, providing more flexibility for owners
Steel is easier to modify and reinforce if architectural changes are made to a facility over its life
Steel is lightweight and can reduce foundation costs
Steel is durable, long-lasting and recyclable (AISC 1999)

## Slide 5
<number>
Unique Aspects of Steel Construction
Procurement and management of structural steel is similar to other materials, but there are some unique aspects to steel construction:
Steel is fabricated off-site (above left)
On-site erection is a rapid process (above right)
This gives use of structural steel some scheduling advantages
Coordination of all parties is essential for achieving potential advantages
(AISC 1999)

## Slide 6
<number>
Forces On Structures
Forces from gravity, wind, and seismic events are imposed on all structures
Forces that act vertically are gravity loads
Forces that act horizontally, such as stability, wind and seismic events (the focus of this discussion) require lateral load resisting systems to be built into structures
As lateral loads are applied to a structure, horizontal diaphragms (floors and roofs) transfer the load to the lateral load resisting system
(AISC 2002)
Structural Steel Frame Elevation

## Slide 7
<number>
Initial System Planning
The type of lateral load resisting system to be used in a structure should be considered early in the planning stage
Lateral stability as well as architectural needs must be met
The three common lateral load resisting systems are:
Braced Frames
Rigid Frames
Shear Walls
(Adapted from AISC 2002)
2
1
1
3
Shear Wall
Rigid Frame
Chevron Braced
X Braced
Rigid Horiz. Diaphragm (Floor or Roof)

## Slide 8
<number>
Braced Frames and Rigid Frames
This presentation focuses on braced frames (left) and rigid frames (right)

## Slide 9
<number>
Steel Frame Connection Types
The Specification for Structural Steel Buildings (AISC 2005) defines two types of connections:
Simple Connections (above left)
Moment Connections (above right)
  Fully-Restrained and Partially-Restrained
Notes: <number>

## Slide 10
<number>
All connections have a certain amount of rigidity
Simple connections (A above) have some rigidity, but are assumed to be free to rotate
Partially-Restrained moment connections (B and C above) are designed to be semi-rigid
Fully-Restrained moment connections (D and E above) are designed to be fully rigid
Steel Frame Connection Types
(AISC)

## Slide 11
<number>
Simple Connections
Designed as flexible connections
Connections are assumed to be free to rotate
Vertical shear forces are the primary forces transferred by the connection
Require a separate bracing system for lateral stability
The following few slides show some common simple framing connections

## Slide 12
<number>
Common Simple Connections
Single Plate Connection (Shear Tab)
A plate is welded to the supporting member and bolted to the web of the supported beam
Double Angle Connection
The in-plane pair of legs are attached to the web of the supported beam and the out-of-plane pair of legs to the flange or web of the supporting member
(Green, Sputo, and Veltri)

## Slide 13
<number>
Common Simple Connections
Shear End Plate Connection
A plate is welded perpendicular to the end of the supported web and attached to the supporting member
Single Angle Connection
One leg is attached to the web of the supported beam and the other leg to the flange or web of the supporting member
(Green, Sputo, and Veltri)

## Slide 14
<number>
Common Simple Connections
Seated Connection
An angle is mounted with one leg vertical against the supporting column, and the other leg provides a “seat” upon which the beam is mounted
A stabilizer connection is also provided at the top of the web
Tee Connection
The stem of a WT section is connected to the supported member and the flange attached to the supporting member
(Green, Sputo, and Veltri)

## Slide 15
<number>
Moment Connections
Designed as rigid connections which allow little or no rotation
  Used in rigid frames
Moment and vertical shear forces are transferred through the connection
Two types of moment connections are permitted:
  Fully-Restrained
  Partially-Restrained

## Slide 16
<number>
Moment Connections

## Slide 17
<number>
Common FR Connections
Bolted Flange Plate Connection
Welded Flange Plate Connection
Top and bottom flange-plates connect the flanges of the supported member to the supporting column
A single plate connection is used to transfer vertical shear forces
(Green, Sputo, and Veltri)

## Slide 18
<number>
Common FR Connections
Bolted Extended End-Plate Connection
A plate is welded to the flanges and web of the supported member and bolted with high-strength bolts to the supporting column
Welded Flange Connection
Complete-joint-penetration groove welds directly connect the top and bottom flanges of the supported member to the supporting column
A shear connection on the web is used to transfer vertical shear forces
(Green, Sputo, and Veltri)

## Slide 19
<number>
Common PR Connections
PR Moment Connection – Wind Only
A double angle simple connection transfers vertical shear forces while top and bottom flange plates resist moment forces produced by wind
Note that the size of the flange plate is relatively small in comparison to the beam flange
Top and Bottom Angle with Shear End Plate Connection
Angles are bolted or welded to the top and bottom flanges of the supported member and to the supporting column
A shear end plate on the web is used to transfer vertical shear forces

## Slide 20
<number>
Rigid Frames
Rigid frames, utilizing moment connections, are well suited for specific types of buildings where diagonal bracing is not feasible or does not fit the architectural design
Rigid frames generally cost more than braced frames (AISC 2002)

## Slide 21
<number>
Braced Frames
Diagonal bracing creates stable triangular configurations within the steel building frame (AISC 2002)
“Braced frames are often the most economical method of resisting wind loads in multi-story buildings (AISC 1991).”
Some structures, like the one pictured above, are designed with a combination braced and rigid frame to take advantage of the benefits of both
Notes: <number>

## Slide 22
<number>
Structural steel frames require temporary bracing during construction
Temporary bracing is placed before plumbing up the structural frame
This gives the structure temporary lateral stability
Temporary bracing is removed by the erector
Temporary Bracing

## Slide 23
<number>
In a braced frame, temporary bracing is removed after final bolt-up is complete and the permanent bracing system is in place
In a rigid frame, temporary bracing is removed after final bolt-up is complete
Temporary Bracing

## Slide 24
<number>
Concentric Braced Frames
Bracing is concentric when the center lines of the bracing members intersect
Common concentric braced frames used in buildings today include:
X brace (above left)
Two story X’s
X bracing is possibly the most common type of bracing
Bracing can allow a building to have access through the brace line depending on configuration (AISC 2002)
Chevron (above right)
Single diagonals

## Slide 25
<number>
X Bracing
The diagonal members of X bracing go into tension and compression similar to a truss
The multi-floor building frame elevation shown above has just one braced bay, but it may be necessary to brace many bays along a column line
With this in mind it is important to determine the locations of the braced bays in a structure early in a project
(AISC 2002)
X-braced building elevation
X Bracing
Typical floor plan with X bracing
1st Floor
Floor
Floor
Roof

## Slide 26
<number>
X Bracing
Connections for X bracing are located at beam to column joints
Bracing connections may require relatively large gusset plates at the beam to column joint
The restriction of space in these areas may have an impact on the mechanical and plumbing systems as well as some architectural features
(AISC 2002)

## Slide 27
<number>
Chevron Bracing
The members used in Chevron bracing are designed for both tension and compression forces
Chevron bracing allows for doorways or corridors through the bracing lines in a structure
A multi-floor frame elevation using Chevron bracing is shown above
(AISC 2002)
Chevron Bracing
Typical floor plan with Chevron bracing
Elevation with several bracing configurations
Roof
1st Floor
Floor
Floor
Chevron
“V”
“K”

## Slide 28
<number>
Chevron bracing members use two types of connections
The floor level connection may use a gusset plate much like the connection on X braced frames
The bracing members are connected to the beam/girder at the top and converge to a common point
If gusset plates are used, it is important to consider their size when laying-out mechanical and plumbing systems that pass through braced bays (AISC 2002)
Chevron Bracing

## Slide 29
<number>
Eccentrically Braced Frames
Eccentric bracing is commonly used in seismic regions and allows for doorways and corridors in the braced bays
The difference between Chevron bracing and eccentric bracing is the space between the bracing members at the top gusset connection
  In an eccentrically braced frame bracing members connect to separate points on the beam/girder
The beam/girder segment or “link” between the bracing members absorbs energy from seismic activity through plastic deformation (AISC 2002)
Eccentric Brace
Link
Gusset
Eccentric brace with typical brace to beam connection
(Adapted from AISC 2002)
Beam or Girder
Stiffeners

## Slide 30
<number>
Eccentrically Braced Frames
Eccentrically braced frames look similar to frames with Chevron bracing
A similar V shaped bracing configuration is used
(AISC 2002)

## Slide 31
<number>
Eccentrically Braced Frames
Eccentric single diagonals may also be used to brace a frame
(EERC 1997)

## Slide 32
<number>
Combination Frames
As shown above (left) a braced frame deflects like a cantilever beam while a moment resisting frame deflects more or less consistently from top to bottom
By combining the two systems, reduced deflections can be realized
The combination frame is shown above right
(AISC 1991)
Chevron braced
Moment resisting
Combination Frame
Bracing
Moment frame

## Slide 33
<number>
Combination Frames
The plot shows the moment resisting frame alone, the braced frame alone, and the combined frame
The same wind load was used for each frame model (AISC 1991)
(AISC 1991)
O = Combined Frames
X = Chevron or “K” Bracing
 = Moment Resisting

## Slide 34
<number>
Structural Steel: The Material of Choice

## Slide 35
<number>
References
AISC. (n.d.). Steel Connections: Behavior and Practice [35mm Slide Show with Script]. American Institute of Steel Construction, Inc. Chicago, IL.
AISC. (1989). Specification for Structural Steel Buildings, Allowable Stress Design and Plastic Design, 9th ed. American Institute of Steel Construction, Inc. Chicago, IL.
AISC. (1991). Design Guide for Low- and Medium-Rise Steel Buildings. American Institute of Steel Construction, Inc. Chicago, IL.
AISC. (1999). Load and Resistance Factor Design Specification For Structural Steel Buildings. American Institute of Steel Construction, Inc. Chicago, IL.
AISC. (2002). Designing With Structural Steel – A guide For Architects. American Institute of Steel Construction, Inc. Chicago, IL .
Earthquake Engineering Research Center, (EERC). (1997). W. G. Godden Structural Engineering Slide Library. Godden J119. Available at: http://nisee.berkeley.edu/bertero/html/recent_developments_in_seismic_design_and_construction.html. Viewed August, 2004.
Green, P. S., Sputo, T., and Veltri, P. (n.d.). Connections Teaching Toolkit – A Teaching Guide for Structural Steel Connections. American Institute of Steel Construction, Inc. Chicago, IL.
Notes: <number>