## Doc
"ASCE705W" --- ASCE 7-05 CODE WIND ANALYSIS PROGRAM
Program Description:
"ASCE705W" is a spreadsheet program written in MS-Excel for the purpose of wind loading analysis for buildings
and structures per the ASCE 7-05 Code. Specifically, wind pressure coefficients and related and required
parameters are selected or calculated in order to compute the net design wind pressures.
This program is a workbook consisting of eleven (11) worksheets, described as follows:
Worksheet Name | Description
Doc | This documentation sheet
Simplified | Analysis using simplified method for low-rise buildings with h <= 60’
MWFRS (Low-Rise) | Main Wind-Force Resisting System for low-rise buildings with h <= 60’
MWFRS (Any Ht.) | Main Wind-Force Resisting System for buildings of any height
MWFRS (Case 2) | Main Wind-Force Resisting System - Figure 6-9, Load Case 2
MWFRS (Case 4) | Main Wind-Force Resisting System - Figure 6-9, Load Case 4
Wall C&C | Analysis of wall Components and Cladding
Roof C&C | Analysis of roof Components and Cladding
Stacks & Tanks | Analysis of cantilevered chimneys, stacks, and vertical tanks
Open Structures (no roof) | Analysis of open structures without roofs
Wind Map | Basic wind speed map (Figure 6-1 of ASCE 7-05 Code)
Program Assumptions and Limitations:
1. Worksheet for "Simplified" analysis is applicable for low-rise buildings meeting the criteria of Section 6.4.1.
2. In the worksheet for Simplified analysis, the design MWFRS wind load is calculated for each direction.
The design MWFRS load is assumed to be the total wind load on either the width or the length of the
building respectively.
3. Worksheet for "MWFRS (Low-Rise)" is applicable for low-rise buildings as defined in Section 6.2.
4. Worksheets for "MWFRS (Any Ht.)", "Wall C&C", and "Roof C&C" are applicable for buildings with mean roof
heights of up to 500 feet.
5. In worksheets for "MWFRS (Any Ht.)", "Wall C&C", and "Roof C&C" the user may opt to utilize user designated
steps in height, 'z', in determining the wind pressure distribution.
6. Worksheets for "MWFRS (Any Ht.)", "Stacks & Tanks", and "Open Structures" can handle “rigid” as well as
“flexible” buildings and structures. For “rigid” buildings or structures, this program uses the smaller value of
either 0.85 or the calculated value from Section 6.5.8.1 of the Code for the gust effect factor, 'G'. For “flexible”
buildings or structures, this program calculates the gust effect factor, ‘Gf’, per Section 6.5.8.2 of the Code
based on the assumed formula for the fundamental period of vibration from Section 12.8.2.1 of the Code,
where the exponent 'x' in the formula T = Ct*h^x is assumed to be 0.75. In the "Stacks & Tanks" worksheet,
this program uses the specific formula from the ASCE 7-05 Code Commentary for the fundament (mode 1)
natural frequency for a thin-walled cantilevered vessel.
7. Worksheets for "Wall C&C" and "Roof C&C" are applicable for flat roof buildings, gable roof buildings with
roof angles <= 45 degrees, and monoslope roof buildings with roof angles <= 3 degrees.
8. Worksheet for "Stacks & Tanks" is applicable for cantilevered structures up to 600 feet tall.
9. Worksheet for "Open Structures" is applicable for open structures without roofs up to 500 feet
tall. This can be utilized for open process-type structures as well as pipe/utility racks and bridges.
10. This program uses the equations listed in the reference, “Guide to the Use of the Wind Load Provisions of
ASCE 7-05” by Kishor C. Mehta and William L. Coulbourne for determining the external wind pressure
coefficients, ‘GCp’, used in the Wall C&C and Roof C&C worksheets.
11. This program contains numerous “comment boxes” which contain a wide variety of information including
explanations of input or output items, equations used, data tables, etc. (Note: presence of a “comment box”
is denoted by a “red triangle” in the upper right-hand corner of a cell. Merely move the mouse pointer to the
desired cell to view the contents of that particular "comment box".)

## Simplified
WIND LOADING ANALYSIS - MWFRS and Components/Cladding | [11 empty] | CALCULATIONS: | [81 empty] | Version 1.4
Per ASCE 7-05 Code for Low-Rise, Enclosed Buildings with h <= 60' and Roof q <= 45o
Using Method 1: Simplified Procedure (Section 6.4) | [9 empty] | 85 |  | For Transverse Direction:
Job Name: |  |  |  |  | Subject: |  |  |  |  | 90 |  | Main Wind Force Resisting System - Method 1 |  |  |  |  | for h <= 60 ft. | [20 empty] | Components and Cladding - Method 1 |  |  |  |  | for h <= 60 ft. | [11 empty] | Components and Cladding - Method 1 |  |  |  |  | for h <= 60 ft. | [11 empty] | Components and Cladding - Method 1 |  |  |  |  | for h <= 60 ft. | [12 empty] | Adjustment Factor
Job Number: |  |  |  |  | Originator: |  | Checker: |  |  | 100 |  | Figure 6-2 |  | Design Wind Pressures | [11 empty] | Select values from Figure 6-2 based on wind speed and roof angle: | [11 empty] | Figure 6-3 |  | Design Wind Pressures | [14 empty] | Figure 6-3 |  | Design Wind Pressures | [14 empty] | Figure 6-3 |  | Design Wind Pressures | [15 empty] | for Building Height and Exposure, l |  |  |  |  | ASCE 7-05 Figure 6-2 (pages 38-39): | [13 empty] | ASCE 7-05 Figure 6-3 (pages 42 to 43): | [26 empty] | ASCE 7-05 Figure 6-3 (page 44): | [14 empty] | ASCE 7-05 Figures 6-2 and 6-3 (pages 40 and 44):
[10 empty] | 105 |  | Enclosed Buildings |  |  |  |  | WALLS and ROOFS | [9 empty] | Roof Angle, q = | 5.5722 | deg. | for Gable: q = ATAN((hr-he)/(W/2)) , for Monoslope: q = ATAN((hr-he)/W) | [7 empty] | Enclosed Buildings |  |  |  |  | WALLS and ROOFS | [11 empty] | Enclosed Buildings |  |  |  |  | WALLS and ROOFS | [11 empty] | Enclosed Buildings |  |  |  |  | WALLS and ROOFS | [12 empty] | Mean Roof | Exposure |  |  |  | Main Wind Force Resisting System - Method 1 |  |  |  |  | for h <= 60 ft. | [8 empty] | Components and Cladding - Method 1 |  |  |  |  | for h <= 60 ft. | [21 empty] | Components and Cladding - Method 1 |  |  |  |  | for h <= 60 ft. | [9 empty] | Adjustment Factor
Input Data: | [9 empty] | 110 |  | Simplified Design Wind Pressure, ps30 (psf) (Exposure B at h = 30 ft. with Iw = 1.0) | [14 empty] | Mean Roof Ht., h = | 15 | ft. | h = he for q < 10 deg. , h = (hr+he)/2 for q >= 10 deg. | [7 empty] | Net Design Positive (+) Wind Pressure, pnet30 (psf) (Exposure B at h = 30 ft. with I = 1.0) | [16 empty] | Net Design Negative (-) Wind Pressure, pnet30 (psf) (Exposure B at h = 30 ft. with I = 1.0) | [16 empty] | Roof Overhang Net Design Wind Pressure, pnet30 (psf) (Exposure B at h = 30 ft. with I = 1.0) | [16 empty] | Index | Height, h (ft.) | B | C | D |  | Figure 6-2 |  | Design Wind Pressures | [11 empty] | Figure 6-3 |  | Design Wind Pressures | [24 empty] | Figure 6-3 |  | Design Wind Pressures | [12 empty] | for Building Height and Exposure, l
| Wind Speed, V = | 90 | mph (Wind Map, Figure 6-1) | [6 empty] | 120 |  | Basic Wind | Roof | Load | Zones | [22 empty] | Roof and | Zone | Eff. Wind | Basic Wind Speed, V (mph) | [13 empty] | Roof and | Zone | Eff. Wind | Basic Wind Speed, V (mph) | [13 empty] | Roof and | Zone | Eff. Wind | Basic Wind Speed, V (mph) | [13 empty] | 1 | 15 | 1 | 1.21 | 1.47 |  | Enclosed Buildings |  |  |  |  | WALLS and ROOFS | [8 empty] | Enclosed Buildings |  |  |  |  | WALLS and ROOFS | [21 empty] | Enclosed Buildings |  |  |  |  | WALLS and ROOFS | [9 empty] | Mean Roof | Exposure
| Bldg. Classification = | II | (Table 1-1 Occupancy Category) | [6 empty] | 125 |  | Speed, V | Angle | Case | Horizontal Pressures |  |  |  | Vertical Pressures |  |  |  | Overhangs | [14 empty] | Walls |  | Area (ft.^2) | 85 | 90 | 100 | 105 | 110 | 120 | 125 | 130 | 140 | 145 | 150 | 170 | For V = | 90 | Walls |  | Area (ft.^2) | 85 | 90 | 100 | 105 | 110 | 120 | 125 | 130 | 140 | 145 | 150 | 170 | For V = | 90 | Walls |  | Area (ft.^2) | 85 | 90 | 100 | 105 | 110 | 120 | 125 | 130 | 140 | 145 | 150 | 170 | For V = | 90 | 2 | 20 | 1 | 1.29 | 1.55 |  | Simplified Design Wind Pressure, ps30 (psf) (Exposure B at h = 30 ft. with Iw = 1.0) | [13 empty] | Net Design Positive (+) Wind Pressure, pnet30 (psf) (Exposure B at h = 30 ft. with I = 1.0) | [26 empty] | Roof Overhang Net Design Wind Pressure, pnet30 (psf) (Exposure B at h = 30 ft. with I = 1.0) | [14 empty] | Height, h (ft.) | B | C | D
| Exposure Category = | B | (Sect. 6.5.6) | [6 empty] | 130 | Index | (mph) | (deg.) |  | A | B | C | D | E | F | G | H | Eoh | Goh | Index |  | q | A | B | C | D | E | F | G | H | Eoh | Goh |  | 1 | 10 | 5.3 | 5.9 | 7.3 | 8.1 | 8.9 | 10.5 | 11.4 | 12.4 | 14.3 | 15.4 | 16.5 | 21.1 | Select: | 5.9 |  | 1 | 10 | -13 | -14.6 | -18 | -19.8 | -21.8 | -25.9 | -28.1 | -30.4 | -35.3 | -37.8 | -40.5 | -52 | Select: | -14.6 |  | 2 | 10 | -21 | -21 | -25.9 | -28.7 | -31.4 | -37.3 | -40.6 | -43.8 | -50.8 | -54.6 | -58.3 | -74.9 | Select: | -21 | 3 | 25 | 1 | 1.35 | 1.61 |  | Basic Wind | Roof | Roof | Load | Zones | [9 empty] | Roof and | Zone | Eff. Wind | Basic Wind Speed, V (mph) | [23 empty] | Roof and | Zone | Eff. Wind | Basic Wind Speed, V (mph) | [11 empty] | 15 | 1 | 1.21 | 1.47
| Ridge Height, hr = | 19 | ft. (hr >= he) | [6 empty] | 140 | 1 |  | 0 | 1 | 11.5 | -5.9 | 7.6 | -3.5 | -13.8 | -7.8 | -9.6 | -6.1 | -19.3 | -15.1 | 1 | [13 empty] | 1 | 20 | 5 | 5.6 | 6.9 | 7.6 | 8.3 | 9.9 | 10.7 | 11.6 | 13.4 | 14.4 | 15.4 | 19.8 | Select: | 5.6 |  | 1 | 20 | -12.7 | -14.2 | -17.5 | -19.3 | -21.2 | -25.2 | -27.4 | -29.6 | -34.4 | -36.9 | -39.4 | -50.7 | Select: | -14.2 |  | 2 | 20 | -20.6 | -20.6 | -25.5 | -28.2 | -30.8 | -36.7 | -39.9 | -43 | -49.9 | -53.6 | -57.3 | -73.6 | Select: | -20.6 | 4 | 30 | 1 | 1.4 | 1.66 |  | Speed, V | Angle | Rise in | Case | Horizontal Pressures |  |  |  | Vertical Pressures |  |  |  | Overhangs |  | Walls |  | Area (ft.^2) | 85 |  | 90 |  | 100 |  | 105 |  | 110 |  | 120 |  | 125 |  | 130 |  | 140 |  | 145 |  | 150 |  | 170 |  | Walls |  | Area (ft.^2) | 85 | 90 | 100 | 105 | 110 | 120 | 125 | 130 | 140 | 145 | 150 | 170 | 20 | 1 | 1.29 | 1.55
| Eave Height, he = | 15 | ft. (he <= hr) | [6 empty] | 145 | 2 |  | 5 | 1 | 11.5 | -5.9 | 7.6 | -3.5 | -13.8 | -7.8 | -9.6 | -6.1 | -19.3 | -15.1 | 2 | [13 empty] | 1 | 50 | 4.5 | 5.1 | 6.3 | 6.9 | 7.6 | 9 | 9.8 | 10.6 | 12.3 | 13.1 | 14.1 | 18.1 | Select: | 5.1 |  | 1 | 50 | -12.2 | -13.7 | -16.9 | -18.7 | -20.5 | -24.4 | -26.4 | -28.6 | -33.2 | -35.6 | -38.1 | -48.9 | Select: | -13.7 | Roof | 2 | 50 | -20.1 | -20.1 | -24.9 | -27.5 | -30.1 | -35.8 | -38.9 | -42 | -48.7 | -52.3 | -55.9 | -71.8 | Select: | -20.1 | 5 | 35 | 1.05 | 1.45 | 1.7 |  | (mph) | (deg.) | 12" |  | A | B | C | D | E | F | G | H | Eoh | Goh |  | 1 | 10 | 5.3 | -13 | 5.9 | -14.6 | 7.3 | -18 | 8.1 | -19.8 | 8.9 | -21.8 | 10.5 | -25.9 | 11.4 | -28.1 | 12.4 | -30.4 | 14.3 | -35.3 | 15.4 | -37.8 | 16.5 | -40.5 | 21.1 | -52 |  | 2 | 10 | -21 | -21 | -25.9 | -28.7 | -31.4 | -37.3 | -40.6 | -43.8 | -50.8 | -54.6 | -58.3 | -74.9 | 25 | 1 | 1.35 | 1.61
| Building Width, W = | 41 | ft. (Normal to Building Ridge) | [6 empty] | 150 | 3 |  | 10 | 1 | 12.9 | -5.4 | 8.6 | -3.1 | -13.8 | -8.4 | -9.6 | -6.5 | -19.3 | -15.1 | 3 | 0 | [12 empty] | 1 | 100 | 4.2 | 4.7 | 5.8 | 6.4 | 7 | 8.3 | 9.1 | 9.8 | 11.4 | 12.2 | 13 | 16.7 | Select: | 4.7 |  | 1 | 100 | -11.9 | -13.3 | -16.5 | -18.2 | -19.9 | -23.7 | -25.7 | -27.8 | -32.3 | -34.6 | -37 | -47.6 | Select: | -13.3 | 0 to 7 | 2 | 100 | -19.8 | -19.8 | -24.4 | -27 | -29.5 | -35.1 | -38.2 | -41.2 | -47.8 | -51.4 | -54.9 | -70.5 | Select: | -19.8 | 6 | 40 | 1.09 | 1.49 | 1.74 |  |  | 0 to 5 | Flat | 1 | 11.5 | -5.9 | 7.6 | -3.5 | -13.8 | -7.8 | -9.6 | -6.1 | -19.3 | -15.1 |  | 1 | 20 | 5 | -12.7 | 5.6 | -14.2 | 6.9 | -17.5 | 7.6 | -19.3 | 8.3 | -21.2 | 9.9 | -25.2 | 10.7 | -27.4 | 11.6 | -29.6 | 13.4 | -34.4 | 14.4 | -36.9 | 15.4 | -39.4 | 19.8 | -50.7 |  | 2 | 20 | -20.6 | -20.6 | -25.5 | -28.2 | -30.8 | -36.7 | -39.9 | -43 | -49.9 | -53.6 | -57.3 | -73.6 | 30 | 1 | 1.4 | 1.66
| Building Length, L = | 61 | ft. (Parallel to Building Ridge) | [6 empty] | 170 | 4 |  | 15 | 1 | 14.4 | -4.8 | 9.6 | -2.7 | -13.8 | -9 | -9.6 | -6.9 | -19.3 | -15.1 | 4 | [13 empty] | 2 | 10 | 5.3 | 5.9 | 7.3 | 8.1 | 8.9 | 10.5 | 11.4 | 12.4 | 14.3 | 15.4 | 16.5 | 21.1 | Select: | 5.9 |  | 2 | 10 | -21.8 | -24.4 | -30.2 | -33.3 | -36.5 | -43.5 | -47.2 | -51 | -59.2 | -63.5 | -67.9 | -87.2 | Select: | -24.4 | degrees | 3 | 10 | -34.6 | -34.6 | -42.7 | -47.2 | -51.6 | -61.5 | -66.8 | -72.1 | -83.7 | -89.9 | -96 | -123.4 | Select: | -34.6 | 7 | 45 | 1.12 | 1.53 | 1.78 |  |  | 10 | 2 | 1 | 12.9 | -5.4 | 8.6 | -3.1 | -13.8 | -8.4 | -9.6 | -6.5 | -19.3 | -15.1 |  | 1 | 50 | 4.5 | -12.2 | 5.1 | -13.7 | 6.3 | -16.9 | 6.9 | -18.7 | 7.6 | -20.5 | 9 | -24.4 | 9.8 | -26.4 | 10.6 | -28.6 | 12.3 | -33.2 | 13.1 | -35.6 | 14.1 | -38.1 | 18.1 | -48.9 | Roof | 2 | 50 | -20.1 | -20.1 | -24.9 | -27.5 | -30.1 | -35.8 | -38.9 | -42 | -48.7 | -52.3 | -55.9 | -71.8 | 35 | 1.05 | 1.45 | 1.7
| Roof Type = | Monoslope | (Gable or Monoslope) | [6 empty] | I | 5 |  | 20 | 1 | 15.9 | -4.2 | 10.6 | -2.3 | -13.8 | -9.6 | -9.6 | -7.3 | -19.3 | -15.1 | 5 | [12 empty] | Roof | 2 | 20 | 5 | 5.6 | 6.9 | 7.6 | 8.3 | 9.9 | 10.7 | 11.6 | 13.4 | 14.4 | 15.4 | 19.8 | Select: | 5.6 | Roof | 2 | 20 | -19.5 | -21.8 | -27 | -29.7 | -32.6 | -38.8 | -42.1 | -45.6 | -52.9 | -56.7 | -60.7 | -78 | Select: | -21.8 |  | 3 | 20 | -27.1 | -27.1 | -33.5 | -37 | -40.5 | -48.3 | -52.5 | -56.6 | -65.7 | -70.6 | -75.4 | -96.8 | Select: | -27.1 | 8 | 50 | 1.26 | 1.56 | 1.81 |  |  | 15 | 3 | 1 | 14.4 | -4.8 | 9.6 | -2.7 | -13.8 | -9 | -9.6 | -6.9 | -19.3 | -15.1 |  | 1 | 100 | 4.2 | -11.9 | 4.7 | -13.3 | 5.8 | -16.5 | 6.4 | -18.2 | 7 | -19.9 | 8.3 | -23.7 | 9.1 | -25.7 | 9.8 | -27.8 | 11.4 | -32.3 | 12.2 | -34.6 | 13 | -37 | 16.7 | -47.6 | 0 to 7 | 2 | 100 | -19.8 | -19.8 | -24.4 | -27 | -29.5 | -35.1 | -38.2 | -41.2 | -47.8 | -51.4 | -54.9 | -70.5 | 40 | 1.09 | 1.49 | 1.74
| Topo. Factor, Kzt = | 1 | (Sect. 6.5.7 & Figure 6-4) |  |  |  | Plan |  |  | II | 6 | 85 | 25 | 1 | 14.4 | 2.3 | 10.4 | 2.4 | -6.4 | -8.7 | -4.6 | -7 | -11.9 | -10.1 | 6 | [12 empty] | 0 to 7 | 2 | 50 | 4.5 | 5.1 | 6.3 | 6.9 | 7.6 | 9 | 9.8 | 10.6 | 12.3 | 13.1 | 14.1 | 18.1 | Select: | 5.1 | 0 to 7 | 2 | 50 | -16.4 | -18.4 | -22.7 | -25.1 | -27.5 | -32.7 | -35.5 | -38.4 | -44.5 | -47.8 | -51.1 | -65.7 | Select: | -18.4 |  | 3 | 50 | -17.3 | -17.3 | -21.4 | -23.7 | -25.9 | -30.8 | -33.5 | -36.1 | -41.9 | -45 | -48.1 | -61.8 | Select: | -17.3 | 9 | 55 | 1.19 | 1.59 | 1.84 |  | 85 | 20 | 4 | 1 | 15.9 | -4.2 | 10.6 | -2.3 | -13.8 | -9.6 | -9.6 | -7.3 | -19.3 | -15.1 |  | 2 | 10 | 5.3 | -21.8 | 5.9 | -24.4 | 7.3 | -30.2 | 8.1 | -33.3 | 8.9 | -36.5 | 10.5 | -43.5 | 11.4 | -47.2 | 12.4 | -51 | 14.3 | -59.2 | 15.4 | -63.5 | 16.5 | -67.9 | 21.1 | -87.2 | degrees | 3 | 10 | -34.6 | -34.6 | -42.7 | -47.2 | -51.6 | -61.5 | -66.8 | -72.1 | -83.7 | -89.9 | -96 | -123.4 | 45 | 1.12 | 1.53 | 1.78
| Wall C&C Name = | Wall | (Girt, Siding, Wall, or Fastener) | [6 empty] | III | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -2.4 | -4.7 | -0.7 | -3 | 0 | 0 | 7 | [12 empty] | degrees | 2 | 100 | 4.2 | 4.7 | 5.8 | 6.4 | 7 | 8.3 | 9.1 | 9.8 | 11.4 | 12.2 | 13 | 16.7 | Select: | 4.7 | degrees | 2 | 100 | -14.1 | -15.8 | -19.5 | -21.5 | -23.6 | -28.1 | -30.5 | -33 | -38.2 | -41 | -43.9 | -56.4 | Select: | -15.8 |  | 3 | 100 | -10 | -10 | -12.2 | -13.5 | -14.8 | -17.6 | -19.1 | -20.6 | -23.9 | -25.7 | -27.4 | -35.2 | Select: | -10 | 10 | 60 | 1.22 | 1.62 | 1.87 |  |  | 25 | 6 | 1 | 14.4 | 2.3 | 10.4 | 2.4 | -6.4 | -8.7 | -4.6 | -7 | -11.9 | -10.1 | Roof | 2 | 20 | 5 | -19.5 | 5.6 | -21.8 | 6.9 | -27 | 7.6 | -29.7 | 8.3 | -32.6 | 9.9 | -38.8 | 10.7 | -42.1 | 11.6 | -45.6 | 13.4 | -52.9 | 14.4 | -56.7 | 15.4 | -60.7 | 19.8 | -78 |  | 3 | 20 | -27.1 | -27.1 | -33.5 | -37 | -40.5 | -48.3 | -52.5 | -56.6 | -65.7 | -70.6 | -75.4 | -96.8 | 50 | 1.26 | 1.56 | 1.81
| Wall C&C Eff. Area = | 75 | ft.^2 (for Component/Cladding) | [6 empty] | IV | 8 |  | 30 | 1 | 12.9 | 8.8 | 10.2 | 7 | 1 | -7.8 | 0.3 | -6.7 | -4.5 | -5.2 | 8 | [13 empty] | 3 | 10 | 5.3 | 5.9 | 7.3 | 8.1 | 8.9 | 10.5 | 11.4 | 12.4 | 14.3 | 15.4 | 16.5 | 21.1 | Select: | 5.9 |  | 3 | 10 | -32.8 | -36.8 | -45.4 | -50.1 | -55 | -65.4 | -71 | -76.8 | -89 | -95.5 | -102.2 | -131.3 | Select: | -36.8 |  | 2 | 10 | -27.2 | -27.2 | -33.5 | -37.1 | -40.6 | -48.3 | -52.5 | -56.7 | -65.7 | -70.6 | -75.5 | -96.9 | Select: | -27.2 | [9 empty] | 2 | --- | --- | --- | --- | -2.4 | -4.7 | -0.7 | -3 | --- | --- | 0 to 7 | 2 | 50 | 4.5 | -16.4 | 5.1 | -18.4 | 6.3 | -22.7 | 6.9 | -25.1 | 7.6 | -27.5 | 9 | -32.7 | 9.8 | -35.5 | 10.6 | -38.4 | 12.3 | -44.5 | 13.1 | -47.8 | 14.1 | -51.1 | 18.1 | -65.7 |  | 3 | 50 | -17.3 | -17.3 | -21.4 | -23.7 | -25.9 | -30.8 | -33.5 | -36.1 | -41.9 | -45 | -48.1 | -61.8 | 55 | 1.19 | 1.59 | 1.84
| Roof C&C Name = | Joist | (Purlin, Joist, Decking, or Fastener) | [6 empty] | B | 9 |  |  | 2 | 12.9 | 8.8 | 10.2 | 7 | 5 | -3.9 | 4.3 | -2.8 | -4.5 | -5.2 | 9 | [13 empty] | 3 | 20 | 5 | 5.6 | 6.9 | 7.6 | 8.3 | 9.9 | 10.7 | 11.6 | 13.4 | 14.4 | 15.4 | 19.8 | Select: | 5.6 |  | 3 | 20 | -27.2 | -30.5 | -37.6 | -41.5 | -45.5 | -54.2 | -58.5 | -63.6 | -73.8 | -79.1 | -84.7 | -108.7 | Select: | -30.5 |  | 2 | 20 | -27.2 | -27.2 | -33.5 | -37.1 | -40.6 | -48.3 | -52.5 | -56.7 | -65.7 | -70.6 | -75.5 | -96.9 | Select: | -27.2 |  | h | B | C | D |  |  | 30 to 45 | 7 to 12 | 1 | 12.9 | 8.8 | 10.2 | 7 | 1 | -7.8 | 0.3 | -6.7 | -4.5 | -5.2 | degrees | 2 | 100 | 4.2 | -14.1 | 4.7 | -15.8 | 5.8 | -19.5 | 6.4 | -21.5 | 7 | -23.6 | 8.3 | -28.1 | 9.1 | -30.5 | 9.8 | -33 | 11.4 | -38.2 | 12.2 | -41 | 13 | -43.9 | 16.7 | -56.4 |  | 3 | 100 | -10 | -10 | -12.2 | -13.5 | -14.8 | -17.6 | -19.1 | -20.6 | -23.9 | -25.7 | -27.4 | -35.2 | 60 | 1.22 | 1.62 | 1.87
| Roof C&C Eff. Area = | 205 | ft.^2 (for Component/Cladding) | [6 empty] | C | 10 |  | 45 | 1 | 12.9 | 8.8 | 10.2 | 7 | 1 | -7.8 | 0.3 | -6.7 | -4.5 | -5.2 | 10 | [13 empty] | 3 | 50 | 4.5 | 5.1 | 6.3 | 6.9 | 7.6 | 9 | 9.8 | 10.6 | 12.3 | 13.1 | 14.1 | 18.1 | Select: | 5.1 |  | 3 | 50 | -19.7 | -22.1 | -27.3 | -30.1 | -33.1 | -39.3 | -42.7 | -46.2 | -53.5 | -57.4 | -61.5 | -78.9 | Select: | -22.1 | Roof | 2 | 50 | -27.2 | -27.2 | -33.5 | -37.1 | -40.6 | -48.3 | -52.5 | -56.7 | -65.7 | -70.6 | -75.5 | -96.9 | Select: | -27.2 |  | 15 | 1 | 1.21 | 1.47 |  |  |  |  | 2 | 12.9 | 8.8 | 10.2 | 7 | 5 | -3.9 | 4.3 | -2.8 | -4.5 | -5.2 |  | 3 | 10 | 5.3 | -32.8 | 5.9 | -36.8 | 7.3 | -45.4 | 8.1 | -50.1 | 8.9 | -55 | 10.5 | -65.4 | 11.4 | -71 | 12.4 | -76.8 | 14.3 | -89 | 15.4 | -95.5 | 16.5 | -102.2 | 21.1 | -131.3 |  | 2 | 10 | -27.2 | -27.2 | -33.5 | -37.1 | -40.6 | -48.3 | -52.5 | -56.7 | -65.7 | -70.6 | -75.5 | -96.9
| Overhang Eff. Area = | 0 | ft.^2 (for Component/Cladding) | [6 empty] | D | 11 |  |  | 2 | 12.9 | 8.8 | 10.2 | 7 | 5 | -3.9 | 4.3 | -2.8 | -4.5 | -5.2 | 11 | [13 empty] | 3 | 100 | 4.2 | 4.7 | 5.8 | 6.4 | 7 | 8.3 | 9.1 | 9.8 | 11.4 | 12.2 | 13 | 16.7 | Select: | 4.7 |  | 3 | 100 | -14.1 | -15.8 | -19.5 | -21.5 | -23.6 | -28.1 | -30.5 | -33 | -38.2 | -41 | -43.9 | -56.4 | Select: | -15.8 | 7 to 27 | 2 | 100 | -27.2 | -27.2 | -33.5 | -37.1 | -40.6 | -48.3 | -52.5 | -56.7 | -65.7 | -70.6 | -75.5 | -96.9 | Select: | -27.2 |  | 20 | 1 | 1.29 | 1.55 |  |  | 0 to 5 | Flat | 1 | 12.8 | -6.7 | 8.5 | -4 | -15.4 | -8.8 | -10.7 | -6.8 | -21.6 | -16.9 |  | 3 | 20 | 5 | -27.2 | 5.6 | -30.5 | 6.9 | -37.6 | 7.6 | -41.5 | 8.3 | -45.5 | 9.9 | -54.2 | 10.7 | -58.5 | 11.6 | -63.6 | 13.4 | -73.8 | 14.4 | -79.1 | 15.4 | -84.7 | 19.8 | -108.7 |  | 2 | 20 | -27.2 | -27.2 | -33.5 | -37.1 | -40.6 | -48.3 | -52.5 | -56.7 | -65.7 | -70.6 | -75.5 | -96.9
| Hurricane Region? | N | [7 empty] | Gable | 1 |  | 0 | 1 | 12.8 | -6.7 | 8.5 | -4 | -15.4 | -8.8 | -10.7 | -6.8 | -21.6 | -16.9 | 12 |  | 5 | 12.8 | -6.7 | 8.5 | -4 | -15.4 | -8.8 | -10.7 | -6.8 | -21.6 | -16.9 |  | 1 | 10 | 7.5 | 8.4 | 10.4 | 11.4 | 12.5 | 14.9 | 16.2 | 17.5 | 20.3 | 21.8 | 23.3 | 30 | Select: | 8.4 |  | 1 | 10 | -11.9 | -13.3 | -16.5 | -18.2 | -19.9 | -23.7 | -25.7 | -27.8 | -32.3 | -34.6 | -37 | -47.6 | Select: | -13.3 | degrees | 3 | 10 | -45.7 | -45.7 | -56.4 | -62.4 | -68.3 | -81.2 | -88.3 | -95.3 | -110.6 | -118.8 | -126.9 | -163 | Select: | -45.7 |  | 15 | 1 | 1.21 | 1.47 |  |  | 10 | 2 | 1 | 14.5 | -6 | 9.6 | -3.5 | -15.4 | -9.4 | -10.7 | -7.2 | -21.6 | -16.9 |  | 3 | 50 | 4.5 | -19.7 | 5.1 | -22.1 | 6.3 | -27.3 | 6.9 | -30.1 | 7.6 | -33.1 | 9 | -39.3 | 9.8 | -42.7 | 10.6 | -46.2 | 12.3 | -53.5 | 13.1 | -57.4 | 14.1 | -61.5 | 18.1 | -78.9 | Roof | 2 | 50 | -27.2 | -27.2 | -33.5 | -37.1 | -40.6 | -48.3 | -52.5 | -56.7 | -65.7 | -70.6 | -75.5 | -96.9
[10 empty] | Monoslope | 2 |  | 5 | 1 | 12.8 | -6.7 | 8.5 | -4 | -15.4 | -8.8 | -10.7 | -6.8 | -21.6 | -16.9 | 13 |  | 10 | 14.5 | -6 | 9.6 | -3.5 | -15.4 | -9.4 | -10.7 | -7.2 | -21.6 | -16.9 |  | 1 | 20 | 6.8 | 7.7 | 9.4 | 10.4 | 11.4 | 13.6 | 14.8 | 16 | 18.5 | 19.9 | 21.3 | 27.3 | Select: | 7.7 |  | 1 | 20 | -11.6 | -13 | -16 | -17.6 | -19.4 | -23 | -25 | -27 | -31.4 | -33.7 | -36 | -46.3 | Select: | -13 |  | 3 | 20 | -41.2 | -41.2 | -50.9 | -56.3 | -61.6 | -73.3 | -79.7 | -86 | -99.8 | -107.2 | -114.5 | -147.1 | Select: | -41.2 |  | Use: l = | 1 |  |  |  |  | 15 | 3 | 1 | 16.1 | -5.4 | 10.7 | -3 | -15.4 | -10.1 | -10.7 | -7.7 | -21.6 | -16.9 |  | 3 | 100 | 4.2 | -14.1 | 4.7 | -15.8 | 5.8 | -19.5 | 6.4 | -21.5 | 7 | -23.6 | 8.3 | -28.1 | 9.1 | -30.5 | 9.8 | -33 | 11.4 | -38.2 | 12.2 | -41 | 13 | -43.9 | 16.7 | -56.4 | 7 to 27 | 2 | 100 | -27.2 | -27.2 | -33.5 | -37.1 | -40.6 | -48.3 | -52.5 | -56.7 | -65.7 | -70.6 | -75.5 | -96.9
Resulting Parameters and Net Design Pressures: | [9 empty] | Purlin | 3 |  | 10 | 1 | 14.5 | -6 | 9.6 | -3.5 | -15.4 | -9.4 | -10.7 | -7.2 | -21.6 | -16.9 | 14 | 2 | 5.5722 | 12.9945 | -6.6199 | 8.6259 | -3.9428 | -15.4 | -8.8687 | -10.7 | -6.8458 | -21.6 | -16.9 |  | 1 | 50 | 6 | 6.7 | 8.2 | 9.1 | 10 | 11.9 | 12.9 | 13.9 | 16.1 | 17.3 | 18.5 | 23.8 | Select: | 6.7 |  | 1 | 50 | -11.1 | -12.5 | -15.4 | -17 | -18.6 | -22.2 | -24.1 | -26 | -30.2 | -32.4 | -34.6 | -44.5 | Select: | -12.5 |  | 3 | 50 | -35.3 | -35.3 | -43.6 | -48.2 | -52.8 | -62.8 | -68.3 | -73.7 | -85.5 | -91.8 | -98.1 | -126.1 | Select: | -35.3 | [6 empty] | 90 | 20 | 4 | 1 | 17.8 | -4.7 | 11.9 | -2.6 | -15.4 | -10.7 | -10.7 | -8.1 | -21.6 | -16.9 |  | 1 | 10 | 7.5 | -11.9 | 8.4 | -13.3 | 10.4 | -16.5 | 11.4 | -18.2 | 12.5 | -19.9 | 14.9 | -23.7 | 16.2 | -25.7 | 17.5 | -27.8 | 20.3 | -32.3 | 21.8 | -34.6 | 23.3 | -37 | 30 | -47.6 | degrees | 3 | 10 | -45.7 | -45.7 | -56.4 | -62.4 | -68.3 | -81.2 | -88.3 | -95.3 | -110.6 | -118.8 | -126.9 | -163
| For Transverse Direction: |  |  | (wind perpendicular to ridge) |  |  | Elevation |  |  | Joist | 4 |  | 15 | 1 | 16.1 | -5.4 | 10.7 | -3 | -15.4 | -10.1 | -10.7 | -7.7 | -21.6 | -16.9 | 15 | [13 empty] | 1 | 100 | 5.3 | 5.9 | 7.3 | 8.1 | 8.9 | 10.5 | 11.4 | 12.4 | 14.3 | 15.4 | 16.5 | 21.1 | Select: | 5.9 |  | 1 | 100 | -10.8 | -12.1 | -14.9 | -16.5 | -18.1 | -21.5 | -23.2 | -25.2 | -29.3 | -31.4 | -33.6 | -43.2 | Select: | -12.1 |  | 3 | 100 | -30.9 | -30.9 | -38.1 | -42.1 | -46.1 | -54.9 | -59.7 | -64.4 | -74.7 | -80.3 | -85.8 | -110.1 | Select: | -30.9 | [7 empty] | 25 | 6 | 1 | 16.1 | 2.6 | 11.7 | 2.7 | -7.2 | -9.8 | -5.2 | -7.8 | -13.3 | -11.4 |  | 1 | 20 | 6.8 | -11.6 | 7.7 | -13 | 9.4 | -16 | 10.4 | -17.6 | 11.4 | -19.4 | 13.6 | -23 | 14.8 | -25 | 16 | -27 | 18.5 | -31.4 | 19.9 | -33.7 | 21.3 | -36 | 27.3 | -46.3 |  | 3 | 20 | -41.2 | -41.2 | -50.9 | -56.3 | -61.6 | -73.3 | -79.7 | -86 | -99.8 | -107.2 | -114.5 | -147.1
|  | Roof Angle, q = | 5.5722 | deg. | [5 empty] | Decking | 5 |  | 20 | 1 | 17.8 | -4.7 | 11.9 | -2.6 | -15.4 | -10.7 | -10.7 | -8.1 | -21.6 | -16.9 | 16 | [13 empty] | 2 | 10 | 7.5 | 8.4 | 10.4 | 11.4 | 12.5 | 14.9 | 16.2 | 17.5 | 20.3 | 21.8 | 23.3 | 30 | Select: | 8.4 |  | 2 | 10 | -20.7 | -23.2 | -28.7 | -31.6 | -34.7 | -41.3 | -44.8 | -48.4 | -56.2 | -60.3 | -64.5 | -82.8 | Select: | -23.2 |  | 2 | 10 | -24.7 | -24.7 | -30.5 | -33.7 | -36.9 | -43.9 | -47.7 | -51.5 | -59.8 | -64.2 | -68.6 | -88.1 | Select: | -24.7 | [9 empty] | 2 | --- | --- | --- | --- | -2.7 | -5.3 | -0.7 | -3.4 | --- | --- |  | 1 | 50 | 6 | -11.1 | 6.7 | -12.5 | 8.2 | -15.4 | 9.1 | -17 | 10 | -18.6 | 11.9 | -22.2 | 12.9 | -24.1 | 13.9 | -26 | 16.1 | -30.2 | 17.3 | -32.4 | 18.5 | -34.6 | 23.8 | -44.5 |  | 3 | 50 | -35.3 | -35.3 | -43.6 | -48.2 | -52.8 | -62.8 | -68.3 | -73.7 | -85.5 | -91.8 | -98.1 | -126.1
|  | Mean Roof Ht., h = | 15 | ft. (h = he for q < 10 deg.) | [5 empty] | Fastener | 6 | 90 | 25 | 1 | 16.1 | 2.6 | 11.7 | 2.7 | -7.2 | -9.8 | -5.2 | -7.8 | -13.3 | -11.4 | 17 | [12 empty] | Roof | 2 | 20 | 6.8 | 7.7 | 9.4 | 10.4 | 11.4 | 13.6 | 14.8 | 16 | 18.5 | 19.9 | 21.3 | 27.3 | Select: | 7.7 | Roof | 2 | 20 | -19 | -21.4 | -26.4 | -29.1 | -31.9 | -38 | -41.2 | -44.6 | -51.7 | -55.4 | -59.3 | -76.2 | Select: | -21.4 |  | 2 | 20 | -24 | -24 | -29.6 | -32.7 | -35.8 | -42.6 | -46.3 | -50 | -58 | -62.3 | -66.5 | -85.5 | Select: | -24 | [7 empty] | 30 to 45 | 7 to 12 | 1 | 14.4 | 9.9 | 11.5 | 7.9 | 1.1 | -8.8 | 0.4 | -7.5 | -5.1 | -5.8 |  | 1 | 100 | 5.3 | -10.8 | 5.9 | -12.1 | 7.3 | -14.9 | 8.1 | -16.5 | 8.9 | -18.1 | 10.5 | -21.5 | 11.4 | -23.2 | 12.4 | -25.2 | 14.3 | -29.3 | 15.4 | -31.4 | 16.5 | -33.6 | 21.1 | -43.2 |  | 3 | 100 | -30.9 | -30.9 | -38.1 | -42.1 | -46.1 | -54.9 | -59.7 | -64.4 | -74.7 | -80.3 | -85.8 | -110.1
|  | Adjustment Factor, l = | 1 | (adjusts for height and exposure) | [5 empty] | Girt | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -2.7 | -5.3 | -0.7 | -3.4 | 0 | 0 | 18 | [12 empty] | 7 to 27 | 2 | 50 | 6 | 6.7 | 8.2 | 9.1 | 10 | 11.9 | 12.9 | 13.9 | 16.1 | 17.3 | 18.5 | 23.8 | Select: | 6.7 | 7 to 27 | 2 | 50 | -16.9 | -18.9 | -23.3 | -25.7 | -28.2 | -33.6 | -36.5 | -39.4 | -45.7 | -49.1 | -52.5 | -67.4 | Select: | -18.9 | Roof | 2 | 50 | -23 | -23 | -28.4 | -31.4 | -34.3 | -40.8 | -44.4 | -47.9 | -55.6 | -59.7 | -63.8 | -82 | Select: | -23 | [9 empty] | 2 | 14.4 | 9.9 | 11.5 | 7.9 | 5.6 | -4.3 | 4.8 | -3.1 | -5.1 | -5.8 |  | 2 | 10 | 7.5 | -20.7 | 8.4 | -23.2 | 10.4 | -28.7 | 11.4 | -31.6 | 12.5 | -34.7 | 14.9 | -41.3 | 16.2 | -44.8 | 17.5 | -48.4 | 20.3 | -56.2 | 21.8 | -60.3 | 23.3 | -64.5 | 30 | -82.8 |  | 2 | 10 | -24.7 | -24.7 | -30.5 | -33.7 | -36.9 | -43.9 | -47.7 | -51.5 | -59.8 | -64.2 | -68.6 | -88.1
|  | Importance Factor, I = | 1 | (Table 6-1) | [5 empty] | Siding | 8 |  | 30 | 1 | 14.4 | 9.9 | 11.5 | 7.9 | 1.1 | -8.8 | 0.4 | -7.5 | -5.1 | -5.8 | 19 | [12 empty] | degrees | 2 | 100 | 5.3 | 5.9 | 7.3 | 8.1 | 8.9 | 10.5 | 11.4 | 12.4 | 14.3 | 15.4 | 16.5 | 21.1 | Select: | 5.9 | degrees | 2 | 100 | -15.2 | -17 | -21 | -23.2 | -25.5 | -30.3 | -32.9 | -35.6 | -41.2 | -44.2 | -47.3 | -60.8 | Select: | -17 | 27 to 45 | 2 | 100 | -22.2 | -22.2 | -27.4 | -30.3 | -33.2 | -39.5 | -43 | -46.4 | -53.8 | -57.8 | -61.7 | -79.3 | Select: | -22.2 | [7 empty] | 0 to 5 | Flat | 1 | 15.9 | -8.2 | 10.5 | -4.9 | -19.1 | -10.8 | -13.3 | -8.4 | -26.7 | -20.9 | Roof | 2 | 20 | 6.8 | -19 | 7.7 | -21.4 | 9.4 | -26.4 | 10.4 | -29.1 | 11.4 | -31.9 | 13.6 | -38 | 14.8 | -41.2 | 16 | -44.6 | 18.5 | -51.7 | 19.9 | -55.4 | 21.3 | -59.3 | 27.3 | -76.2 |  | 2 | 20 | -24 | -24 | -29.6 | -32.7 | -35.8 | -42.6 | -46.3 | -50 | -58 | -62.3 | -66.5 | -85.5
|  | Wall & Roof End Zone Width, a = | 4.1 | ft. (use: "2*a" for MWFRS, "a" for C&C) | [5 empty] | Wall | 9 |  |  | 2 | 14.4 | 9.9 | 11.5 | 7.9 | 5.6 | -4.3 | 4.8 | -3.1 | -5.1 | -5.8 | 20 | [13 empty] | 3 | 10 | 7.5 | 8.4 | 10.4 | 11.4 | 12.5 | 14.9 | 16.2 | 17.5 | 20.3 | 21.8 | 23.3 | 30 | Select: | 8.4 |  | 3 | 10 | -30.6 | -34.3 | -42.4 | -46.7 | -51.3 | -61 | -66.2 | -71.6 | -83.1 | -89.1 | -95.4 | -122.5 | Select: | -34.3 | degrees | 3 | 10 | -24.7 | -24.7 | -30.5 | -33.7 | -36.9 | -43.9 | -47.7 | -51.5 | -59.8 | -64.2 | -68.6 | -88.1 | Select: | -24.7 | [7 empty] | 10 | 2 | 1 | 17.9 | -7.4 | 11.9 | -4.3 | -19.1 | -11.6 | -13.3 | -8.9 | -26.7 | -20.9 | 7 to 27 | 2 | 50 | 6 | -16.9 | 6.7 | -18.9 | 8.2 | -23.3 | 9.1 | -25.7 | 10 | -28.2 | 11.9 | -33.6 | 12.9 | -36.5 | 13.9 | -39.4 | 16.1 | -45.7 | 17.3 | -49.1 | 18.5 | -52.5 | 23.8 | -67.4 | Roof | 2 | 50 | -23 | -23 | -28.4 | -31.4 | -34.3 | -40.8 | -44.4 | -47.9 | -55.6 | -59.7 | -63.8 | -82
[10 empty] | Fastener | 10 |  | 45 | 1 | 14.4 | 9.9 | 11.5 | 7.9 | 1.1 | -8.8 | 0.4 | -7.5 | -5.1 | -5.8 | 21 | [13 empty] | 3 | 20 | 6.8 | 7.7 | 9.4 | 10.4 | 11.4 | 13.6 | 14.8 | 16 | 18.5 | 19.9 | 21.3 | 27.3 | Select: | 7.7 |  | 3 | 20 | -28.6 | -32.1 | -39.6 | -43.7 | -47.9 | -57.1 | -61.9 | -67 | -77.7 | -83.3 | -89.2 | -114.5 | Select: | -32.1 |  | 3 | 20 | -24 | -24 | -29.6 | -32.7 | -35.8 | -42.6 | -46.3 | -50 | -58 | -62.3 | -66.5 | -85.5 | Select: | -24 | [7 empty] | 15 | 3 | 1 | 19.9 | -6.6 | 13.3 | -3.8 | -19.1 | -12.4 | -13.3 | -9.5 | -26.7 | -20.9 | degrees | 2 | 100 | 5.3 | -15.2 | 5.9 | -17 | 7.3 | -21 | 8.1 | -23.2 | 8.9 | -25.5 | 10.5 | -30.3 | 11.4 | -32.9 | 12.4 | -35.6 | 14.3 | -41.2 | 15.4 | -44.2 | 16.5 | -47.3 | 21.1 | -60.8 | 27 to 45 | 2 | 100 | -22.2 | -22.2 | -27.4 | -30.3 | -33.2 | -39.5 | -43 | -46.4 | -53.8 | -57.8 | -61.7 | -79.3
| Transverse MWFRS Net Pressures, ps (psf) | [6 empty] | ps = l*Kzt*I*ps30 |  | Y | 11 |  |  | 2 | 14.4 | 9.9 | 11.5 | 7.9 | 5.6 | -4.3 | 4.8 | -3.1 | -5.1 | -5.8 | 22 | [13 empty] | 3 | 50 | 6 | 6.7 | 8.2 | 9.1 | 10 | 11.9 | 12.9 | 13.9 | 16.1 | 17.3 | 18.5 | 23.8 | Select: | 6.7 |  | 3 | 50 | -26 | -29.1 | -36 | -39.7 | -43.5 | -51.8 | -56.2 | -60.8 | -70.5 | -75.7 | -81 | -104 | Select: | -29.1 |  | 3 | 50 | -23 | -23 | -28.4 | -31.4 | -34.3 | -40.8 | -44.4 | -47.9 | -55.6 | -59.7 | -63.8 | -82 | Select: | -23 | [6 empty] | 100 | 20 | 4 | 1 | 22 | -5.8 | 14.6 | -3.2 | -19.1 | -13.3 | -13.3 | -10.1 | -26.7 | -20.9 |  | 3 | 10 | 7.5 | -30.6 | 8.4 | -34.3 | 10.4 | -42.4 | 11.4 | -46.7 | 12.5 | -51.3 | 14.9 | -61 | 16.2 | -66.2 | 17.5 | -71.6 | 20.3 | -83.1 | 21.8 | -89.1 | 23.3 | -95.4 | 30 | -122.5 | degrees | 3 | 10 | -24.7 | -24.7 | -30.5 | -33.7 | -36.9 | -43.9 | -47.7 | -51.5 | -59.8 | -64.2 | -68.6 | -88.1
| Location |  |  | Direction | Zone | Load Case 1 | Load Case 2 | (ps30 from Fig. 6-2) |  | N | 1 |  | 0 | 1 | 15.9 | -8.2 | 10.5 | -4.9 | -19.1 | -10.8 | -13.3 | -8.4 | -26.7 | -20.9 | 23 | [13 empty] | 3 | 100 | 5.3 | 5.9 | 7.3 | 8.1 | 8.9 | 10.5 | 11.4 | 12.4 | 14.3 | 15.4 | 16.5 | 21.1 | Select: | 5.9 |  | 3 | 100 | -24 | -26.9 | -33.2 | -36.6 | -40.2 | -47.9 | -51.9 | -56.2 | -65.1 | -69.9 | -74.8 | -96 | Select: | -26.9 |  | 3 | 100 | -22.2 | -22.2 | -24.4 | -28.8 | -33.2 | -39.5 | -43 | -46.4 | -53.8 | -57.8 | -61.7 | -79.3 | Select: | -22.2 | [7 empty] | 25 | 6 | 1 | 19.9 | 3.2 | 14.4 | 3.3 | -8.8 | -12 | -6.4 | -9.7 | -16.5 | -14 |  | 3 | 20 | 6.8 | -28.6 | 7.7 | -32.1 | 9.4 | -39.6 | 10.4 | -43.7 | 11.4 | -47.9 | 13.6 | -57.1 | 14.8 | -61.9 | 16 | -67 | 18.5 | -77.7 | 19.9 | -83.3 | 21.3 | -89.2 | 27.3 | -114.5 |  | 3 | 20 | -24 | -24 | -29.6 | -32.7 | -35.8 | -42.6 | -46.3 | -50 | -58 | -62.3 | -66.5 | -85.5
| A = end zone of wall |  |  | Horizontal | A | 12.9945 | --- |  |  |  | 2 |  | 5 | 1 | 15.9 | -8.2 | 10.5 | -4.9 | -19.1 | -10.8 | -13.3 | -8.4 | -26.7 | -20.9 | 24 | [13 empty] | 1 | 10 | 11.9 | 13.3 | 16.5 | 18.2 | 19.9 | 23.7 | 25.7 | 27.8 | 32.3 | 34.6 | 37 | 47.6 | Select: | 13.3 |  | 1 | 10 | -13 | -14.6 | -18 | -19.8 | -21.8 | -25.9 | -28.1 | -30.4 | -35.3 | -37.8 | -40.5 | -52 | Select: | -14.6 | [26 empty] | 2 | --- | --- | --- | --- | -3.4 | -6.6 | -0.9 | -4.2 | --- | --- |  | 3 | 50 | 6 | -26 | 6.7 | -29.1 | 8.2 | -36 | 9.1 | -39.7 | 10 | -43.5 | 11.9 | -51.8 | 12.9 | -56.2 | 13.9 | -60.8 | 16.1 | -70.5 | 17.3 | -75.7 | 18.5 | -81 | 23.8 | -104 |  | 3 | 50 | -23 | -23 | -28.4 | -31.4 | -34.3 | -40.8 | -44.4 | -47.9 | -55.6 | -59.7 | -63.8 | -82
| B = end zone of roof |  |  | Horizontal | B | 0 | --- |  |  |  | 3 |  | 10 | 1 | 17.9 | -7.4 | 11.9 | -4.3 | -19.1 | -11.6 | -13.3 | -8.9 | -26.7 | -20.9 | 25 | 0 | [12 empty] | 1 | 20 | 11.6 | 13 | 16 | 17.6 | 19.4 | 23 | 25 | 27 | 31.4 | 33.7 | 36 | 46.3 | Select: | 13 |  | 1 | 20 | -12.3 | -13.8 | -17.1 | -18.8 | -20.7 | -24.6 | -26.7 | -28.9 | -33.5 | -35.9 | -38.4 | -49.3 | Select: | -13.8 | [24 empty] | 30 to 45 | 7 to 12 | 1 | 17.8 | 12.2 | 14.2 | 9.8 | 1.4 | -10.8 | 0.5 | -9.3 | -6.3 | -7.2 |  | 3 | 100 | 5.3 | -24 | 5.9 | -26.9 | 7.3 | -33.2 | 8.1 | -36.6 | 8.9 | -40.2 | 10.5 | -47.9 | 11.4 | -51.9 | 12.4 | -56.2 | 14.3 | -65.1 | 15.4 | -69.9 | 16.5 | -74.8 | 21.1 | -96 |  | 3 | 100 | -22.2 | -22.2 | -24.4 | -28.8 | -33.2 | -39.5 | -43 | -46.4 | -53.8 | -57.8 | -61.7 | -79.3
| C = interior zone of wall |  |  | Horizontal | C | 8.6259 | --- |  |  |  | 4 |  | 15 | 1 | 19.9 | -6.6 | 13.3 | -3.8 | -19.1 | -12.4 | -13.3 | -9.5 | -26.7 | -20.9 | 26 | [13 empty] | 1 | 50 | 11.1 | 12.5 | 15.4 | 17 | 18.6 | 22.2 | 24.1 | 26 | 30.2 | 32.4 | 34.6 | 44.5 | Select: | 12.5 |  | 1 | 50 | -11.5 | -12.8 | -15.9 | -17.5 | -19.2 | -22.8 | -24.8 | -26.8 | -31.1 | -33.3 | -35.7 | -45.8 | Select: | -12.8 | Components & Cladding - Overhang Pressures: | [25 empty] | 2 | 17.8 | 12.2 | 14.2 | 9.8 | 6.9 | -5.3 | 5.9 | -3.8 | -6.3 | -7.2 |  | 1 | 10 | 11.9 | -13 | 13.3 | -14.6 | 16.5 | -18 | 18.2 | -19.8 | 19.9 | -21.8 | 23.7 | -25.9 | 25.7 | -28.1 | 27.8 | -30.4 | 32.3 | -35.3 | 34.6 | -37.8 | 37 | -40.5 | 47.6 | -52
| D = interior zone of roof |  |  | Horizontal | D | 0 | --- |  |  |  | 5 |  | 20 | 1 | 22 | -5.8 | 14.6 | -3.2 | -19.1 | -13.3 | -13.3 | -10.1 | -26.7 | -20.9 | 27 | [13 empty] | 1 | 100 | 10.8 | 12.1 | 14.9 | 16.5 | 18.1 | 21.5 | 23.3 | 25.2 | 29.3 | 31.4 | 33.6 | 43.2 | Select: | 12.1 |  | 1 | 100 | -18.8 | -12.1 | -14.9 | -16.5 | -18.1 | -21.5 | -23.3 | -25.2 | -29.3 | -31.4 | -33.6 | -43.2 | Select: | -12.1 | Roof (0 - 7 deg.): | [23 empty] | 0 to 5 | Flat | 1 | 17.5 | -9 | 11.6 | -5.4 | -21.1 | -11.9 | -14.7 | -9.3 | -29.4 | -23 |  | 1 | 20 | 11.6 | -12.3 | 13 | -13.8 | 16 | -17.1 | 17.6 | -18.8 | 19.4 | -20.7 | 23 | -24.6 | 25 | -26.7 | 27 | -28.9 | 31.4 | -33.5 | 33.7 | -35.9 | 36 | -38.4 | 46.3 | -49.3
| E = end zone of windward roof |  |  | Vertical | E | -15.4 | --- |  |  |  | 6 | 100 | 25 | 1 | 19.9 | 3.2 | 14.4 | 3.3 | -8.8 | -12 | -6.4 | -9.7 | -16.5 | -14 | 28 | [13 empty] | 2 | 10 | 11.9 | 13.3 | 16.5 | 18.2 | 19.9 | 23.7 | 25.7 | 27.8 | 32.3 | 34.6 | 37 | 47.6 | Select: | 13.3 |  | 2 | 10 | -15.2 | -17 | -21 | -23.2 | -25.5 | -30.3 | -32.9 | -35.6 | -41.2 | -44.2 | -47.3 | -60.8 | Select: | -17 |  | 2(-) = | -21 | psf | [20 empty] | 10 | 2 | 1 | 19.7 | -8.2 | 13.1 | -4.7 | -21.1 | -12.8 | -14.7 | -9.8 | -29.4 | -23 |  | 1 | 50 | 11.1 | -11.5 | 12.5 | -12.8 | 15.4 | -15.9 | 17 | -17.5 | 18.6 | -19.2 | 22.2 | -22.8 | 24.1 | -24.8 | 26 | -26.8 | 30.2 | -31.1 | 32.4 | -33.3 | 34.6 | -35.7 | 44.5 | -45.8
| F = end zone of leeward roof |  |  | Vertical | F | -8.8687 | --- |  |  |  | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -3.4 | -6.6 | -0.9 | -4.2 | 0 | 0 | 29 | [12 empty] | Roof | 2 | 20 | 11.6 | 13 | 16 | 17.6 | 19.4 | 23 | 25 | 27 | 31.4 | 33.7 | 36 | 46.3 | Select: | 13 | Roof | 2 | 20 | -14.5 | -16.3 | -20.1 | -22.2 | -24.3 | -29 | -31.4 | -34 | -39.4 | -42.3 | -45.3 | -58.1 | Select: | -16.3 |  | 3(-) = | -34.6 | psf | [20 empty] | 15 | 3 | 1 | 21.9 | -7.3 | 14.7 | -4.2 | -21.1 | -13.7 | -14.7 | -10.5 | -29.4 | -23 |  | 1 | 100 | 10.8 | -18.8 | 12.1 | -12.1 | 14.9 | -14.9 | 16.5 | -16.5 | 18.1 | -18.1 | 21.5 | -21.5 | 23.3 | -23.3 | 25.2 | -25.2 | 29.3 | -29.3 | 31.4 | -31.4 | 33.6 | -33.6 | 43.2 | -43.2
| G = interior zone of windward roof |  |  | Vertical | G | -10.7 | --- |  |  |  | 8 |  | 30 | 1 | 17.8 | 12.2 | 14.2 | 9.8 | 1.4 | -10.8 | 0.5 | -9.3 | -6.3 | -7.2 | 30 | [12 empty] | 27 to 45 | 2 | 50 | 11.1 | 12.5 | 15.4 | 17 | 18.6 | 22.2 | 24.1 | 26 | 30.2 | 32.4 | 34.6 | 44.5 | Select: | 12.5 | 27 to 45 | 2 | 50 | -13.7 | -15.3 | -18.9 | -20.8 | -22.9 | -27.2 | -29.5 | -32 | -37.1 | -39.8 | -42.5 | -54.6 | Select: | -15.3 | Roof (7 - 27 deg.): | [22 empty] | 105 | 20 | 4 | 1 | 24.3 | -8.4 | 16.1 | -3.5 | -21.1 | -14.7 | -14.7 | -11.1 | -29.4 | -23 |  | 2 | 10 | 11.9 | -15.2 | 13.3 | -17 | 16.5 | -21 | 18.2 | -23.2 | 19.9 | -25.5 | 23.7 | -30.3 | 25.7 | -32.9 | 27.8 | -35.6 | 32.3 | -41.2 | 34.6 | -44.2 | 37 | -47.3 | 47.6 | -60.8
| H = interior zone of leeward roof |  |  | Vertical | H | -6.8458 | --- |  |  |  | 9 |  |  | 2 | 17.8 | 12.2 | 14.2 | 9.8 | 6.9 | -5.3 | 5.9 | -3.8 | -6.3 | -7.2 | 31 | [12 empty] | degrees | 2 | 100 | 10.8 | 12.1 | 14.9 | 16.5 | 18.1 | 21.5 | 23.2 | 25.2 | 29.3 | 31.4 | 33.6 | 43.2 | Select: | 12.1 | degrees | 2 | 100 | -13 | -14.6 | -18 | -19.8 | -21.8 | -25.9 | -28.1 | -30.4 | -35.3 | -37.8 | -40.5 | -52 | Select: | -14.6 |  | 2(-) = | -27.2 | psf | [20 empty] | 25 | 6 | 1 | 21.9 | 3.5 | 15.9 | 3.5 | -9.7 | -7.1 | -7.1 | -10.7 | -18.2 | -15.4 | Roof | 2 | 20 | 11.6 | -14.5 | 13 | -16.3 | 16 | -20.1 | 17.6 | -22.2 | 19.4 | -24.3 | 23 | -29 | 25 | -31.4 | 27 | -34 | 31.4 | -39.4 | 33.7 | -42.3 | 36 | -45.3 | 46.3 | -58.1
[11 empty] | 10 |  | 45 | 1 | 17.8 | 12.2 | 14.2 | 9.8 | 1.4 | -10.8 | 0.5 | -9.3 | -6.3 | -7.2 | 32 | [13 empty] | 3 | 10 | 11.9 | 13.3 | 16.5 | 18.2 | 19.9 | 23.7 | 25.7 | 27.8 | 32.3 | 34.6 | 37 | 47.6 | Select: | 13.3 |  | 3 | 10 | -15.2 | -17 | -21 | -23.2 | -25.5 | -30.3 | -32.9 | -35.6 | -41.2 | -44.2 | -47.3 | -60.8 | Select: | -17 |  | 3(-) = | -45.7 | psf | [22 empty] | 2 | --- | --- | --- | --- | -3.7 | -1 | -1 | -4.6 | --- | --- | 27 to 45 | 2 | 50 | 11.1 | -13.7 | 12.5 | -15.3 | 15.4 | -18.9 | 17 | -20.8 | 18.6 | -22.9 | 22.2 | -27.2 | 24.1 | -29.5 | 26 | -32 | 30.2 | -37.1 | 32.4 | -39.8 | 34.6 | -42.5 | 44.5 | -54.6
| For Longitudinal Direction: |  |  | (wind parallel to ridge) | [6 empty] | 11 |  |  | 2 | 17.8 | 12.2 | 14.2 | 9.8 | 6.9 | -5.3 | 5.9 | -3.8 | -6.3 | -7.2 | 33 | [13 empty] | 3 | 20 | 11.6 | 13 | 16 | 17.6 | 19.4 | 23 | 25 | 27 | 31.4 | 33.7 | 36 | 46.3 | Select: | 13 |  | 3 | 20 | -14.5 | -16.3 | -20.1 | -22.2 | -24.3 | -29 | -31.4 | -34 | -39.4 | -42.3 | -45.3 | -58.1 | Select: | -16.3 | Roof (20 - 45 deg.): | [23 empty] | 30 to 45 | 7 to 12 | 1 | 19.6 | 13.5 | 10.8 | 10.8 | 1.5 | 0.6 | 0.6 | -10.3 | -6.9 | -7.9 | degrees | 2 | 100 | 10.8 | -13 | 12.1 | -14.6 | 14.9 | -18 | 16.5 | -19.8 | 18.1 | -21.8 | 21.5 | -25.9 | 23.2 | -28.1 | 25.2 | -30.4 | 29.3 | -35.3 | 31.4 | -37.8 | 33.6 | -40.5 | 43.2 | -52
|  | Roof Angle, q = | 0 | deg. (assumed) | [6 empty] | 1 |  | 0 | 1 | 17.5 | -9 | 11.6 | -5.4 | -21.1 | -11.9 | -14.7 | -9.3 | -29.4 | -23 | 34 | [13 empty] | 3 | 50 | 11.1 | 12.5 | 15.4 | 17 | 18.6 | 22.2 | 24.1 | 26 | 30.2 | 32.4 | 34.6 | 44.5 | Select: | 12.5 |  | 3 | 50 | -13.7 | -15.3 | -18.9 | -20.8 | -22.9 | -27.2 | -29.5 | -32 | -37.1 | -39.8 | -42.5 | -54.6 | Select: | -15.3 |  | 2(-) = | -24.7 | psf | [22 empty] | 2 | 19.6 | 13.5 | 10.8 | 10.8 | 7.6 | 6.5 | 6.5 | -4.2 | -6.9 | -7.9 |  | 3 | 10 | 11.9 | -15.2 | 13.3 | -17 | 16.5 | -21 | 18.2 | -23.2 | 19.9 | -25.5 | 23.7 | -30.3 | 25.7 | -32.9 | 27.8 | -35.6 | 32.3 | -41.2 | 34.6 | -44.2 | 37 | -47.3 | 47.6 | -60.8
|  | Mean Roof Ht., h = | 17 | ft. (h = (hr+he)/2) | [6 empty] | 2 |  | 5 | 1 | 17.5 | -9 | 11.6 | -5.4 | -21.1 | -11.9 | -14.7 | -9.3 | -29.4 | -23 | 35 | [13 empty] | 3 | 100 | 10.8 | 12.1 | 14.9 | 16.5 | 18.1 | 21.5 | 23.3 | 25.2 | 29.3 | 31.4 | 33.6 | 43.2 | Select: | 12.1 |  | 3 | 100 | -13 | -14.6 | -18 | -19.8 | -21.8 | -25.9 | -28.1 | -30.4 | -35.3 | -37.8 | -40.5 | -52 | Select: | -14.6 |  | 3(-) = | -24.7 | psf | [20 empty] | 0 to 5 | Flat | 1 | 19.2 | -10 | 12.7 | -5.9 | -23.1 | -13.1 | -16 | -10.1 | -32.3 | -25.3 |  | 3 | 20 | 11.6 | -14.5 | 13 | -16.3 | 16 | -20.1 | 17.6 | -22.2 | 19.4 | -24.3 | 23 | -29 | 25 | -31.4 | 27 | -34 | 31.4 | -39.4 | 33.7 | -42.3 | 36 | -45.3 | 46.3 | -58.1
|  | Adjustment Factor, l = | 1 | (adjusts for height and exposure) | [6 empty] | 3 |  | 10 | 1 | 19.7 | -8.2 | 13.1 | -4.7 | -21.1 | -12.8 | -14.7 | -9.8 | -29.4 | -23 | 36 | 0 | [12 empty] | 4 | 10 | 13 | 14.6 | 18 | 19.8 | 21.8 | 25.9 | 28.1 | 30.4 | 35.3 | 37.8 | 40.5 | 52 | Select: | 14.6 |  | 4 | 10 | -14.1 | -15.8 | -19.5 | -21.5 | -23.6 | -28.1 | -30.5 | -33 | -38.2 | -41 | -43.9 | -56.4 | Select: | -15.8 | [24 empty] | 10 | 2 | 1 | 21.6 | -9 | 14.4 | -5.2 | -23.1 | -14.1 | -16 | -10.8 | -32.3 | -25.3 |  | 3 | 50 | 11.1 | -13.7 | 12.5 | -15.3 | 15.4 | -18.9 | 17 | -20.8 | 18.6 | -22.9 | 22.2 | -27.2 | 24.1 | -29.5 | 26 | -32 | 30.2 | -37.1 | 32.4 | -39.8 | 34.6 | -42.5 | 44.5 | -54.6
[11 empty] | 4 |  | 15 | 1 | 21.9 | -7.3 | 14.7 | -4.2 | -21.1 | -13.7 | -14.7 | -10.5 | -29.4 | -23 | 37 | [13 empty] | 4 | 20 | 12.4 | 13.9 | 17.2 | 18.9 | 20.8 | 24.7 | 26.8 | 29 | 33.7 | 36.1 | 38.7 | 49.6 | Select: | 13.9 |  | 4 | 20 | -13.5 | -15.1 | -18.7 | -20.6 | -22.6 | -26.9 | -29.2 | -31.6 | -36.7 | -39.3 | -42.1 | -54.1 | Select: | -15.1 | [24 empty] | 15 | 3 | 1 | 24.1 | -8 | 16 | -4.6 | -23.1 | -15.1 | -16 | -11.5 | -32.3 | -25.3 |  | 3 | 100 | 10.8 | -13 | 12.1 | -14.6 | 14.9 | -18 | 16.5 | -19.8 | 18.1 | -21.8 | 21.5 | -25.9 | 23.3 | -28.1 | 25.2 | -30.4 | 29.3 | -35.3 | 31.4 | -37.8 | 33.6 | -40.5 | 43.2 | -52
| Longitudinal MWFRS Net Pressures, ps (psf) | [6 empty] | ps = l*Kzt*I*ps30 |  |  | 5 |  | 20 | 1 | 24.3 | -8.4 | 16.1 | -3.5 | -21.1 | -14.7 | -14.7 | -11.1 | -29.4 | -23 | 38 | [13 empty] | 4 | 50 | 11.6 | 13 | 16.1 | 17.8 | 19.5 | 23.2 | 25.2 | 27.2 | 31.6 | 33.9 | 36.2 | 46.6 | Select: | 13 |  | 4 | 50 | -12.7 | -14.3 | -17.6 | -19.4 | -21.3 | -25.4 | -27.5 | -29.8 | -34.6 | -37.1 | -39.7 | -51 | Select: | -14.3 | [23 empty] | 110 | 20 | 4 | 1 | 26.6 | -7 | 17.7 | -3.9 | -23.1 | -16 | -16 | -12.2 | -32.3 | -25.3 |  | 4 | 10 | 13 | -14.1 | 14.6 | -15.8 | 18 | -19.5 | 19.8 | -21.5 | 21.8 | -23.6 | 25.9 | -28.1 | 28.1 | -30.5 | 30.4 | -33 | 35.3 | -38.2 | 37.8 | -41 | 40.5 | -43.9 | 52 | -56.4
| Location |  |  | Direction | Zone | Load Case 1 | Load Case 2 | (ps30 from Fig. 6-2) |  |  | 6 | 105 | 25 | 1 | 21.9 | 3.5 | 15.9 | 3.5 | -9.7 | -7.1 | -7.1 | -10.7 | -18.2 | -15.4 | 39 | [13 empty] | 4 | 100 | 11.1 | 12.4 | 15.3 | 16.9 | 18.5 | 22 | 23.9 | 25.9 | 30 | 32.2 | 34.4 | 44.2 | Select: | 12.4 |  | 4 | 100 | -12.2 | -13.6 | -16.8 | -18.5 | -20.4 | -24.2 | -26.3 | -28.4 | -33 | -35.4 | -37.8 | -48.6 | Select: | -13.6 | [24 empty] | 25 | 6 | 1 | 24.1 | 3.9 | 17.4 | 4 | -10.7 | -14.6 | -7.7 | -11.7 | -19.9 | -17 |  | 4 | 20 | 12.4 | -13.5 | 13.9 | -15.1 | 17.2 | -18.7 | 18.9 | -20.6 | 20.8 | -22.6 | 24.7 | -26.9 | 26.8 | -29.2 | 29 | -31.6 | 33.7 | -36.7 | 36.1 | -39.3 | 38.7 | -42.1 | 49.6 | -54.1
| A = end zone of wall |  |  | Horizontal | A | 12.8 | --- |  |  |  | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -3.7 | -1 | -1 | -4.6 | 0 | 0 | 40 | [12 empty] | Wall | 4 | 500 | 9.7 | 10.9 | 13.4 | 14.8 | 16.2 | 19.3 | 21 | 22.7 | 26.3 | 28.2 | 30.2 | 38.8 | Select: | 10.9 | Wall | 4 | 500 | -10.8 | -12.1 | -14.9 | -16.5 | -18.1 | -21.5 | -23.3 | -25.2 | -29.3 | -31.4 | -33.6 | -43.2 | Select: | -12.1 | [26 empty] | 2 | --- | --- | --- | --- | -4.1 | -7.9 | -1.1 | -5.1 | --- | --- |  | 4 | 50 | 11.6 | -12.7 | 13 | -14.3 | 16.1 | -17.6 | 17.8 | -19.4 | 19.5 | -21.3 | 23.2 | -25.4 | 25.2 | -27.5 | 27.2 | -29.8 | 31.6 | -34.6 | 33.9 | -37.1 | 36.2 | -39.7 | 46.6 | -51
| B = end zone of roof |  |  | Horizontal | B | 0 | --- |  |  |  | 8 |  | 30 | 1 | 19.6 | 13.5 | 10.8 | 10.8 | 1.5 | 0.6 | 0.6 | -10.3 | -6.9 | -7.9 | 41 | [13 empty] | 5 | 10 | 13 | 14.6 | 18 | 19.8 | 21.8 | 25.9 | 28.1 | 30.4 | 35.3 | 37.8 | 40.5 | 52 | Select: | 14.6 |  | 5 | 10 | -17.4 | -19.5 | -24.1 | -26.6 | -29.1 | -34.7 | -37.6 | -40.7 | -47.2 | -50.6 | -54.2 | -69.6 | Select: | -19.5 | [24 empty] | 30 to 45 | 7 to 12 | 1 | 21.6 | 14.8 | 17.2 | 11.8 | 1.7 | -13.1 | 0.6 | -11.3 | -7.6 | -8.7 |  | 4 | 100 | 11.1 | -12.2 | 12.4 | -13.6 | 15.3 | -16.8 | 16.9 | -18.5 | 18.5 | -20.4 | 22 | -24.2 | 23.9 | -26.3 | 25.9 | -28.4 | 30 | -33 | 32.2 | -35.4 | 34.4 | -37.8 | 44.2 | -48.6
| C = interior zone of wall |  |  | Horizontal | C | 8.5 | --- |  |  |  | 9 |  |  | 2 | 19.6 | 13.5 | 10.8 | 10.8 | 7.6 | 6.5 | 6.5 | -4.2 | -6.9 | -7.9 | 42 | [13 empty] | 5 | 20 | 12.4 | 13.9 | 17.2 | 18.9 | 20.8 | 24.7 | 26.8 | 29 | 33.7 | 36.1 | 38.7 | 49.6 | Select: | 13.9 |  | 5 | 20 | -16.2 | -18.2 | -22.5 | -24.8 | -27.2 | -32.4 | -35.1 | -38 | -44 | -47.2 | -50.5 | -64.9 | Select: | -18.2 | [26 empty] | 2 | 21.6 | 14.8 | 17.2 | 11.8 | 8.3 | -6.5 | 7.2 | -4.6 | -7.6 | -8.7 | Wall | 4 | 500 | 9.7 | -10.8 | 10.9 | -12.1 | 13.4 | -14.9 | 14.8 | -16.5 | 16.2 | -18.1 | 19.3 | -21.5 | 21 | -23.3 | 22.7 | -25.2 | 26.3 | -29.3 | 28.2 | -31.4 | 30.2 | -33.6 | 38.8 | -43.2
| D = interior zone of roof |  |  | Horizontal | D | 0 | --- |  |  |  | 10 |  | 45 | 1 | 19.6 | 13.5 | 10.8 | 10.8 | 1.5 | 0.6 | 0.6 | -10.3 | -6.9 | -7.9 | 43 | [13 empty] | 5 | 50 | 11.6 | 13 | 16.1 | 17.8 | 19.5 | 23.2 | 25.2 | 27.2 | 31.6 | 33.9 | 36.2 | 46.6 | Select: | 13 |  | 5 | 50 | -14.7 | -16.5 | -20.3 | -22.4 | -24.6 | -29.3 | -31.8 | -34.3 | -39.8 | -42.7 | -45.7 | -58.7 | Select: | -16.5 | [24 empty] | 0 to 5 | Flat | 1 | 22.8 | -11.9 | 15.1 | -7 | -27.4 | -15.6 | -19.1 | -12.1 | -38.4 | -30.1 |  | 5 | 10 | 13 | -17.4 | 14.6 | -19.5 | 18 | -24.1 | 19.8 | -26.6 | 21.8 | -29.1 | 25.9 | -34.7 | 28.1 | -37.6 | 30.4 | -40.7 | 35.3 | -47.2 | 37.8 | -50.6 | 40.5 | -54.2 | 52 | -69.6
| E = end zone of windward roof |  |  | Vertical | E | -15.4 | --- |  |  |  | 11 |  |  | 2 | 19.6 | 13.5 | 10.8 | 10.8 | 7.6 | 6.5 | 6.5 | -4.2 | -6.9 | -7.9 | 44 | [13 empty] | 5 | 100 | 11.1 | 12.4 | 15.3 | 16.9 | 18.5 | 22 | 23.9 | 25.9 | 30 | 32.2 | 34.4 | 44.2 | Select: | 12.4 |  | 5 | 100 | -13.5 | -15.1 | -18.7 | -20.6 | -22.6 | -26.9 | -29.2 | -31.6 | -36.7 | -39.3 | -42.1 | -54.1 | Select: | -15.1 | [24 empty] | 10 | 2 | 1 | 25.8 | -10.7 | 17.1 | -6.2 | -27.4 | -16.8 | -19.1 | -12.9 | -38.4 | -30.1 |  | 5 | 20 | 12.4 | -16.2 | 13.9 | -18.2 | 17.2 | -22.5 | 18.9 | -24.8 | 20.8 | -27.2 | 24.7 | -32.4 | 26.8 | -35.1 | 29 | -38 | 33.7 | -44 | 36.1 | -47.2 | 38.7 | -50.5 | 49.6 | -64.9
| F = end zone of leeward roof |  |  | Vertical | F | -8.8 | --- |  |  |  | 1 |  | 0 | 1 | 19.2 | -10 | 12.7 | -5.9 | -23.1 | -13.1 | -16 | -10.1 | -32.3 | -25.3 | 45 | [13 empty] | 5 | 500 | 9.7 | 10.9 | 13.4 | 14.8 | 16.2 | 19.3 | 21 | 22.7 | 26.3 | 28.2 | 30.2 | 38.8 | Select: | 10.9 |  | 5 | 500 | -10.8 | -12.1 | -14.9 | -16.5 | -18.1 | -21.5 | -23.2 | -25.2 | -29.3 | -31.1 | -33.6 | -43.2 | Select: | -12.1 | [24 empty] | 15 | 3 | 1 | 29.7 | -9.5 | 19.1 | -5.4 | -27.4 | -17.9 | -19.1 | -13.7 | -38.4 | -30.1 |  | 5 | 50 | 11.6 | -14.7 | 13 | -16.5 | 16.1 | -20.3 | 17.8 | -22.4 | 19.5 | -24.6 | 23.2 | -29.3 | 25.2 | -31.8 | 27.2 | -34.3 | 31.6 | -39.8 | 33.9 | -42.7 | 36.2 | -45.7 | 46.6 | -58.7
| G = interior zone of windward roof |  |  | Vertical | G | -10.7 | --- |  |  |  | 2 |  | 5 | 1 | 19.2 | -10 | 12.7 | -5.9 | -23.1 | -13.1 | -16 | -10.1 | -32.3 | -25.3 | 46 | [69 empty] | 120 | 20 | 4 | 1 | 31.6 | -8.3 | 21.1 | -4.6 | -27.4 | -19.1 | -19.1 | -14.5 | -38.4 | -30.1 |  | 5 | 100 | 11.1 | -13.5 | 12.4 | -15.1 | 15.3 | -18.7 | 16.9 | -20.6 | 18.5 | -22.6 | 22 | -26.9 | 23.9 | -29.2 | 25.9 | -31.6 | 30 | -36.7 | 32.2 | -39.3 | 34.4 | -42.1 | 44.2 | -54.1
| H = interior zone of leeward roof |  |  | Vertical | H | -6.8 | --- |  |  |  | 3 |  | 10 | 1 | 21.6 | -9 | 14.4 | -5.2 | -23.1 | -14.1 | -16 | -10.8 | -32.3 | -25.3 | 47 | 0 | [69 empty] | 25 | 6 | 1 | 28.6 | 4.6 | 20.7 | 4.7 | -12.7 | -17.3 | -9.2 | -13.9 | -23.7 | -20.2 |  | 5 | 500 | 9.7 | -10.8 | 10.9 | -12.1 | 13.4 | -14.9 | 14.8 | -16.5 | 16.2 | -18.1 | 19.3 | -21.5 | 21 | -23.2 | 22.7 | -25.2 | 26.3 | -29.3 | 28.2 | -31.1 | 30.2 | -33.6 | 38.8 | -43.2
[9 empty] | (continued) |  | 4 |  | 15 | 1 | 24.1 | -8 | 16 | -4.6 | -23.1 | -15.1 | -16 | -11.5 | -32.3 | -25.3 | 48 | [12 empty] | Components & Cladding - Positive Pressures: | [16 empty] | Components & Cladding - Negative Pressures: | [42 empty] | 2 | --- | --- | --- | --- | -4.8 | -9.4 | -1.3 | -6 | --- | ---
[11 empty] | 5 |  | 20 | 1 | 26.6 | -7 | 17.7 | -3.9 | -23.1 | -16 | -16 | -12.2 | -32.3 | -25.3 | 49 | [12 empty] | Roof (0 - 7 deg.): | 1(+) = | 4.7 | psf | [13 empty] | Roof (0 - 7 deg.): | 1(-) = | -13.3 | psf | [37 empty] | 30 to 45 | 7 to 12 | 1 | 25.7 | 17.6 | 20.4 | 14 | 2 | -15.6 | 0.7 | -13.4 | -9 | -10.3
| Total Design MWFRS Horizontal Load (kips) | [9 empty] | 6 | 110 | 25 | 1 | 24.1 | 3.9 | 17.4 | 4 | -10.7 | -14.6 | -7.7 | -11.7 | -19.9 | -17 | 50 | [13 empty] | 2(+) = | 4.7 | psf | [14 empty] | 2(-) = | -15.8 | psf | [39 empty] | 2 | 25.7 | 17.6 | 20.4 | 14 | 9.9 | -7.7 | 8.6 | -5.5 | -9 | -10.3
| Transverse |  |  | Longitudinal | [6 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -4.1 | -7.9 | -1.1 | -5.1 | 0 | 0 | 51 | [13 empty] | 3(+) = | 4.7 | psf | [14 empty] | 3(-) = | -15.8 | psf | [37 empty] | 0 to 5 | Flat | 1 | 24.7 | -12.9 | 16.4 | -7.6 | -29.7 | -16.9 | -20.7 | -13.1 | -41.7 | -32.7
| Load Case 1 | Load Case 2 | Min. Load | Load Case 1 | Load Case 2 | Min. Load |  |  |  |  | 8 |  | 30 | 1 | 21.6 | 14.8 | 17.2 | 11.8 | 1.7 | -13.1 | 0.6 | -11.3 | -7.6 | -8.7 | 52 | [12 empty] | Roof (7 - 27 deg.): | 1(+) = | 5.9 | psf | [13 empty] | Roof (7 - 27 deg.): | 1(-) = | -12.1 | psf | [37 empty] | 10 | 2 | 1 | 28 | -11.6 | 18.6 | -6.7 | -29.7 | -18.2 | -20.7 | -14 | -41.7 | -32.7
| 8.9674 | --- | 11.59 | 7.1233 | --- | 6.97 |  |  |  |  | 9 |  |  | 2 | 21.6 | 14.8 | 17.2 | 11.8 | 8.3 | -6.5 | 7.2 | -4.6 | -7.6 | -8.7 | 53 | [13 empty] | 2(+) = | 5.9 | psf | [14 empty] | 2(-) = | -17 | psf | [37 empty] | 15 | 3 | 1 | 31.1 | -10.3 | 20.7 | -5.9 | -29.7 | -19.4 | -20.7 | -14.9 | -41.7 | -32.7
| Formulas: | [9 empty] | 10 |  | 45 | 1 | 21.6 | 14.8 | 17.2 | 11.8 | 1.7 | -13.1 | 0.6 | -11.3 | -7.6 | -8.7 | 54 | [13 empty] | 3(+) = | 5.9 | psf | [14 empty] | 3(-) = | -26.9 | psf | [36 empty] | 125 | 20 | 4 | 1 | 34.3 | -9 | 22.9 | -5 | -29.7 | -20.7 | -20.7 | -15.7 | -41.7 | -32.7
| Ph(Trans) = ((Pc*(L-4*a)+Pa*4*a)*he+(Pd*(L-4*a)+Pb*4*a)*(hr-he))/1000 | [9 empty] | 11 |  |  | 2 | 21.6 | 14.8 | 17.2 | 11.8 | 8.3 | -6.5 | 7.2 | -4.6 | -7.6 | -8.7 | 55 | [12 empty] | Roof (20 - 45 deg.): | 1(+) = | 12.1 | psf | [13 empty] | Roof (20 - 45 deg.): | 1(-) = | -12.1 | psf | [37 empty] | 25 | 6 | 1 | 31 | 5 | 22.5 | 5.1 | -13.8 | -18.8 | -10 | -15.1 | -25.7 | -21.9
| Ph(Trans)(min) = P(min)*L*hr/1000 , where: P(min) = 10.0 psf on projected area | [9 empty] | 1 |  | 0 | 1 | 22.8 | -11.9 | 15.1 | -7 | -27.4 | -15.6 | -19.1 | -12.1 | -38.4 | -30.1 | 56 | [13 empty] | 2(+) = | 12.1 | psf | [14 empty] | 2(-) = | -14.6 | psf | [39 empty] | 2 | --- | --- | --- | --- | -5.2 | -10.2 | -1.4 | -6.5 | --- | ---
| Ph(Long) = (Pa*(hr+he)/2*4*a+Pc*((hr+he)/2*W-(hr+he)/2*4*a))/1000 | [9 empty] | 2 |  | 5 | 1 | 22.8 | -11.9 | 15.1 | -7 | -27.4 | -15.6 | -19.1 | -12.1 | -38.4 | -30.1 | 57 | [13 empty] | 3(+) = | 12.1 | psf | [14 empty] | 3(-) = | -14.6 | psf | [37 empty] | 30 to 45 | 7 to 12 | 1 | 27.9 | 19.1 | 22.1 | 15.2 | 2.2 | -16.9 | 0.8 | -14.5 | -9.8 | -11.2
| Ph(Long)(min) = P(min)*W*(hr+he)/2/1000 , where: P(min) = 10.0 psf on full area | [9 empty] | 3 |  | 10 | 1 | 25.8 | -10.7 | 17.1 | -6.2 | -27.4 | -16.8 | -19.1 | -12.9 | -38.4 | -30.1 | 58 | 0 | [11 empty] | Walls: | 4(+) = | 12.7 | psf | [13 empty] | Walls: | 4(-) = | -13.95 | psf | [39 empty] | 2 | 27.9 | 19.1 | 22.1 | 15.2 | 10.7 | -8.4 | 9.3 | -6 | -9.8 | -11.2
[11 empty] | 4 |  | 15 | 1 | 29.7 | -9.5 | 19.1 | -5.4 | -27.4 | -17.9 | -19.1 | -13.7 | -38.4 | -30.1 | 59 | [13 empty] | 5(+) = | 12.7 | psf | [14 empty] | 5(-) = | -15.8 | psf | [37 empty] | 0 to 5 | Flat | 1 | 26.8 | -13.9 | 17.8 | -8.2 | -32.2 | -18.3 | -22.4 | -14.2 | -45.1 | -35.3
| Components & Cladding Net Pressures, ps (psf) | [6 empty] | pnet = l*Kzt*I*pnet30 |  |  | 5 |  | 20 | 1 | 31.6 | -8.3 | 21.1 | -4.6 | -27.4 | -19.1 | -19.1 | -14.5 | -38.4 | -30.1 | 60 | [70 empty] | 10 | 2 | 1 | 30.2 | -12.5 | 20.1 | -7.3 | -32.2 | -19.7 | -22.4 | -15.1 | -45.1 | -35.3
| Item |  | Location |  | Zone | Pos. (+) | Neg. (-) | (pnet30 from Fig. 6-3) |  |  | 6 | 120 | 25 | 1 | 28.6 | 4.6 | 20.7 | 4.7 | -12.7 | -17.3 | -9.2 | -13.9 | -23.7 | -20.2 | 61 | [70 empty] | 15 | 3 | 1 | 33.7 | -11.2 | 22.4 | -6.4 | -32.2 | -21 | -22.4 | -16.1 | -45.1 | -35.3
| Wall |  | 4 = interior zone of wall |  | 4 | 12.7 | -13.95 |  |  |  | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -4.8 | -9.4 | -1.3 | -6 | 0 | 0 | 62 | [69 empty] | 130 | 20 | 4 | 1 | 37.1 | -9.8 | 24.7 | -5.4 | -32.2 | -22.4 | -22.4 | -17 | -45.1 | -35.3
|  |  | 5 = end zone of wall |  | 5 | 12.7 | -15.8 |  |  |  | 8 |  | 30 | 1 | 25.7 | 17.6 | 20.4 | 14 | 2 | -15.6 | 0.7 | -13.4 | -9 | -10.3 | 63 | [70 empty] | 25 | 6 | 1 | 33.6 | 5.4 | 24.3 | 5.5 | -14.9 | -20.4 | -10.8 | -16.4 | -27.8 | -23.7
|  |  | 1 = interior zone of roof |  | 1 | 4.7 | -13.3 |  |  |  | 9 |  |  | 2 | 25.7 | 17.6 | 20.4 | 14 | 9.9 | -7.7 | 8.6 | -5.5 | -9 | -10.3 | 64 | [72 empty] | 2 | --- | --- | --- | --- | -5.7 | -11.1 | -1.5 | -7.1 | --- | ---
| Roof Joist |  | 2 = end zone of roof |  | 2 | 4.7 | -15.8 |  |  |  | 10 |  | 45 | 1 | 25.7 | 17.6 | 20.4 | 14 | 2 | -15.6 | 0.7 | -13.4 | -9 | -10.3 | 65 | [70 empty] | 30 to 45 | 7 to 12 | 1 | 30.1 | 20.6 | 24 | 16.5 | 2.3 | -18.3 | 0.8 | -15.7 | -10.6 | -12.1
|  |  | 3 = corner zone of roof |  | 3 | 4.7 | -15.8 |  |  |  | 11 |  |  | 2 | 25.7 | 17.6 | 20.4 | 14 | 9.9 | -7.7 | 8.6 | -5.5 | -9 | -10.3 | 66 | [72 empty] | 2 | 30.1 | 20.6 | 24 | 16.5 | 11.6 | -9 | 10 | -6.4 | -10.6 | -12.1
| Roof Overhang |  | 2 = end zone of o.h. |  | 2 | --- | --- |  |  |  | 1 |  | 0 | 1 | 24.7 | -12.9 | 16.4 | -7.6 | -29.7 | -16.9 | -20.7 | -13.1 | -41.7 | -32.7 | 67 | [70 empty] | 0 to 5 | Flat | 1 | 31.1 | -16.1 | 20.6 | -9.6 | -37.3 | -21.2 | -26 | -16.4 | -52.3 | -40.9
|  |  | 3 = corner zone of o.h. |  | 3 | --- | --- |  |  |  | 2 |  | 5 | 1 | 24.7 | -12.9 | 16.4 | -7.6 | -29.7 | -16.9 | -20.7 | -13.1 | -41.7 | -32.7 | 68 | [70 empty] | 10 | 2 | 1 | 35.1 | -14.5 | 23.3 | -8.5 | -37.3 | -22.8 | -26 | -17.5 | -52.3 | -40.9
[11 empty] | 3 |  | 10 | 1 | 28 | -11.6 | 18.6 | -6.7 | -29.7 | -18.2 | -20.7 | -14 | -41.7 | -32.7 | 69 | 0 | [69 empty] | 15 | 3 | 1 | 39 | -12.9 | 26 | -7.4 | -37.3 | -24.4 | -26 | -18.6 | -52.3 | -40.9
Notes: 1. | For Method 1: Simplified Procedure of Section 6.4 to be used for an enclosed low-rise building | [9 empty] | 4 |  | 15 | 1 | 31.1 | -10.3 | 20.7 | -5.9 | -29.7 | -19.4 | -20.7 | -14.9 | -41.7 | -32.7 | 70 | [69 empty] | 140 | 20 | 4 | 1 | 43 | -11.4 | 28.7 | -6.3 | -37.3 | -26 | -26 | -19.7 | -52.3 | -40.9
| to determine the design wind loads, all of the following eight conditions of 6.4.1.1 must be met: | [9 empty] | 5 |  | 20 | 1 | 34.3 | -9 | 22.9 | -5 | -29.7 | -20.7 | -20.7 | -15.7 | -41.7 | -32.7 | 71 | [70 empty] | 25 | 6 | 1 | 39 | 6.3 | 28.2 | 6.4 | -17.3 | -23.6 | -12.5 | -19 | -32.3 | -27.5
| a. Building is a simple diaphragm building, in which wind loads are transmitted through floor | [9 empty] | 6 | 125 | 25 | 1 | 31 | 5 | 22.5 | 5.1 | -13.8 | -18.8 | -10 | -15.1 | -25.7 | -21.9 | 72 | [72 empty] | 2 | --- | --- | --- | --- | -6.6 | -12.8 | -1.8 | -8.2 | --- | ---
| and roof diaphragms to the vertical Main Wind-Force Resisting System (MWFRS). | [9 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -5.2 | -10.2 | -1.4 | -6.5 | 0 | 0 | 73 | [70 empty] | 30 to 45 | 7 to 12 | 1 | 35 | 23.9 | 27.8 | 19.1 | 2.7 | -21.2 | 0.9 | -18.2 | -12.3 | -14
| b. Building is a low-rise building where mean roof height, h <= 60 ft., and h <= min. of L or W. | [9 empty] | 8 |  | 30 | 1 | 27.9 | 19.1 | 22.1 | 15.2 | 2.2 | -16.9 | 0.8 | -14.5 | -9.8 | -11.2 | 74 | [72 empty] | 2 | 35 | 23.9 | 27.8 | 19.1 | 13.4 | -10.5 | 11.7 | -7.5 | -12.3 | -14
| c. Building is enclosed and conforms to wind-borne debris provisions of Section 6.5.9.3. | [9 empty] | 9 |  |  | 2 | 27.9 | 19.1 | 22.1 | 15.2 | 10.7 | -8.4 | 9.3 | -6 | -9.8 | -11.2 | 75 | [70 empty] | 0 to 5 | Flat | 1 | 33.4 | -17.3 | 22.1 | -10.3 | -40 | -22.7 | -27.9 | -17.6 | -56.1 | -43.9
| d. Building is a regular shaped building, having no unusual geometrical irregularity. | [9 empty] | 10 |  | 45 | 1 | 27.9 | 19.1 | 22.1 | 15.2 | 2.2 | -16.9 | 0.8 | -14.5 | -9.8 | -11.2 | 76 | [70 empty] | 10 | 2 | 1 | 37.7 | -15.6 | 25 | -9.1 | -40 | -24.5 | -27.9 | -18.8 | -56.1 | -43.9
| e. Building is not classified as a flexible building so it is considered "rigid". | [9 empty] | 11 |  |  | 2 | 27.9 | 19.1 | 22.1 | 15.2 | 10.7 | -8.4 | 9.3 | -6 | -9.8 | -11.2 | 77 | [70 empty] | 15 | 3 | 1 | 41.8 | -13.8 | 27.9 | -7.9 | -40 | -26.2 | -27.9 | -20 | -56.1 | -43.9
| f. Building is not subject to across-wind loading, vortex shedding, etc. | [9 empty] | 1 |  | 0 | 1 | 26.8 | -13.9 | 17.8 | -8.2 | -32.2 | -18.3 | -22.4 | -14.2 | -45.1 | -35.3 | 78 | [69 empty] | 145 | 20 | 4 | 1 | 46.1 | -12.2 | 30.8 | -6.8 | -40 | -27.9 | -27.9 | -21.1 | -56.1 | -43.9
| g. Building has an approximately symmetrical cross section in each direction with either a | [9 empty] | 2 |  | 5 | 1 | 26.8 | -13.9 | 17.8 | -8.2 | -32.2 | -18.3 | -22.4 | -14.2 | -45.1 | -35.3 | 79 | [70 empty] | 25 | 6 | 1 | 41.8 | 6.8 | 30.3 | 6.9 | -18.6 | -25.3 | -13.4 | -20.4 | -34.6 | -29.5
| flat roof, or gable roof with q <= 45 degrees. | [9 empty] | 3 |  | 10 | 1 | 30.2 | -12.5 | 20.1 | -7.3 | -32.2 | -19.7 | -22.4 | -15.1 | -45.1 | -35.3 | 80 | 0 | [71 empty] | 2 | --- | --- | --- | --- | -7.1 | -13.7 | -1.9 | -8.8 | --- | ---
| h. Building is exempted from torsional load cases or torsional load cases do not control any | [9 empty] | 4 |  | 15 | 1 | 33.7 | -11.2 | 22.4 | -6.4 | -32.2 | -21 | -22.4 | -16.1 | -45.1 | -35.3 | 81 | [70 empty] | 30 to 45 | 7 to 12 | 1 | 37.5 | 25.6 | 29.8 | 20.5 | 2.9 | -22.7 | 1 | -19.5 | -13.2 | -15
| of the MWFRSs of the building. | [9 empty] | 5 |  | 20 | 1 | 37.1 | -9.8 | 24.7 | -5.4 | -32.2 | -22.4 | -22.4 | -17 | -45.1 | -35.3 | 82 | [72 empty] | 2 | 35.7 | 25.6 | 29.8 | 20.5 | 14.4 | -11.3 | 12.6 | -8 | -13.2 | -15
2. | Wind pressures (ps30) in Figure 6-2 and (pnet30) in Figure 6-3 were prepared based on following: | [9 empty] | 6 | 130 | 25 | 1 | 33.6 | 5.4 | 24.3 | 5.5 | -14.9 | -20.4 | -10.8 | -16.4 | -27.8 | -23.7 | 83 | [70 empty] | 0 to 5 | Flat | 1 | 35.7 | -18.5 | 23.7 | -11 | -42.9 | -24.4 | -29.8 | -18.9 | -60 | -47
| a. Mean roof height, h = 30 ft. , Exposure category = B , Importance factor, I =1.0 | [9 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -5.7 | -11.1 | -1.5 | -7.1 | 0 | 0 | 84 | [70 empty] | 10 | 2 | 1 | 40.2 | -16.7 | 26.8 | -9.7 | -42.9 | -26.2 | -29.8 | -20.1 | -60 | -47
| b. Velocity pressure exposure coefficient, Kz = 0.70 | [9 empty] | 8 |  | 30 | 1 | 30.1 | 20.6 | 24 | 16.5 | 2.3 | -18.3 | 0.8 | -15.7 | -10.6 | -12.1 | 85 | [70 empty] | 15 | 3 | 1 | 44.8 | -14.9 | 29.8 | -8.5 | -42.9 | -28 | -29.8 | -21.4 | -60 | -47
| c. Directionality factor, Kd = 0.85 , Topographic factor, Kzt = 1.0 | [9 empty] | 9 |  |  | 2 | 30.1 | 20.6 | 24 | 16.5 | 11.6 | -9 | 10 | -6.4 | -10.6 | -12.1 | 86 | [69 empty] | 150 | 20 | 4 | 1 | 49.4 | -13 | 32.9 | -7.2 | -42.9 | -29.8 | -29.8 | -22.6 | -60 | -47
| d. Internal pressure coefficients, GCpi = +0.18, -0.18 (enclosed building) | [9 empty] | 10 |  | 45 | 1 | 30.1 | 20.6 | 24 | 16.5 | 2.3 | -18.3 | 0.8 | -15.7 | -10.6 | -12.1 | 87 | [70 empty] | 25 | 6 | 1 | 44.8 | 7.2 | 32.4 | 7.4 | -19.9 | -27.1 | -14.4 | -21.6 | -37 | -31.6
| e. MWFRS pressure coeff's. from Figure 6-10, and C&C pressure coeff's. from Figure 6-11. | [9 empty] | 11 |  |  | 2 | 30.1 | 20.6 | 24 | 16.5 | 11.6 | -9 | 10 | -6.4 | -10.6 | -12.1 | 88 | [72 empty] | 2 | --- | --- | --- | --- | -7.5 | -14.7 | -2.1 | -9.4 | --- | ---
| f. MWFRS design wind pressure, Ps = l*Kzt*I*ps30, in psf. | [9 empty] | 1 |  | 0 | 1 | 31.1 | -16.1 | 20.6 | -9.6 | -37.3 | -21.2 | -26 | -16.4 | -52.3 | -40.9 | 89 | [70 empty] | 30 to 45 | 7 to 12 | 1 | 40.1 | 27.4 | 31.9 | 22 | 3.1 | -24.4 | 1 | -20.9 | -14.1 | -16.1
| g. Components & cladding design wind pressure, Pnet = l*Kzt*I*pnet30, in psf. | [9 empty] | 2 |  | 5 | 1 | 31.1 | -16.1 | 20.6 | -9.6 | -37.3 | -21.2 | -26 | -16.4 | -52.3 | -40.9 | 90 | [72 empty] | 2 | 40.1 | 27.4 | 31.9 | 22 | 15.4 | -12 | 13.4 | -8.6 | -14.1 | -16.1
3. | Design wind pressures are net pressures (sum of external and internal pressures). | [9 empty] | 3 |  | 10 | 1 | 35.1 | -14.5 | 23.3 | -8.5 | -37.3 | -22.8 | -26 | -17.5 | -52.3 | -40.9 | 91 | 0 | [69 empty] | 0 to 5 | Flat | 1 | 45.8 | -23.8 | 30.4 | -14.1 | -55.1 | -31.3 | -38.3 | -24.2 | -77.1 | -60.4
4. | Wall net pressure for MWFRS is total for both windward and leeward walls. | [9 empty] | 4 |  | 15 | 1 | 39 | -12.9 | 26 | -7.4 | -37.3 | -24.4 | -26 | -18.6 | -52.3 | -40.9 | 92 | [70 empty] | 10 | 2 | 1 | 51.7 | -21.4 | 34.4 | -12.5 | -55.1 | -33.6 | -38.3 | -25.8 | -77.1 | -60.4
5. | (+) and (-) signs signify wind pressures acting toward & away from respective surfaces. | [9 empty] | 5 |  | 20 | 1 | 43 | -11.4 | 28.7 | -6.3 | -37.3 | -26 | -26 | -19.7 | -52.3 | -40.9 | 92 | [70 empty] | 15 | 3 | 1 | 57.6 | -19.1 | 38.3 | -10.9 | -55.1 | -36 | -38.3 | -27.5 | -77.1 | -60.4
6. | If pressures for Zones "B" and "D" < 0, assume = 0. | [9 empty] | 6 | 140 | 25 | 1 | 39 | 6.3 | 28.2 | 6.4 | -17.3 | -23.6 | -12.5 | -19 | -32.3 | -27.5 | 94 | [69 empty] | 170 | 20 | 4 | 1 | 63.4 | -16.7 | 42.3 | -9.3 | -55.1 | -38.3 | -38.3 | -29.1 | -77.1 | -60.4
7. | For the design of the longitudinal MWFRS use roof angle, q = 0 degrees. | [9 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -6.6 | -12.8 | -1.8 | -8.2 | 0 | 0 | 95 | [70 empty] | 25 | 6 | 1 | 57.5 | 9.3 | 41.6 | 9.5 | -25.6 | -34.8 | -18.5 | -28 | -47.6 | -40.5
8. | Both load cases 1 and 2 are be checked for roof angle, 25 degrees < q <= 45 degrees. | [9 empty] | 8 |  | 30 | 1 | 35 | 23.9 | 27.8 | 19.1 | 2.7 | -21.2 | 0.9 | -18.2 | -12.3 | -14 | 96 | [72 empty] | 2 | --- | --- | --- | --- | -9.7 | -18.9 | -2.6 | -12.1 | --- | ---
9. | The total design MWFRS horizontal load is the total horizontal wind load on either the length (L) | [9 empty] | 9 |  |  | 2 | 35 | 23.9 | 27.8 | 19.1 | 13.4 | -10.5 | 11.7 | -7.5 | -12.3 | -14 | 97 | [70 empty] | 30 to 45 | 7 to 12 | 1 | 51.5 | 35.2 | 41 | 28.2 | 4 | -31.3 | 1.3 | -26.9 | -18.1 | -20.7
| or the width (W) of the building respectively assuming one end zone of a width = 2*a. | [9 empty] | 10 |  | 45 | 1 | 35 | 23.9 | 27.8 | 19.1 | 2.7 | -21.2 | 0.9 | -18.2 | -12.3 | -14 | 98 | [72 empty] | 2 | 51.5 | 35.2 | 41 | 28.2 | 19.8 | -15.4 | 17.2 | -11 | -18.1 | -20.7
10. | Minimum wind load for MWFRS design shall be 10 psf applied to area on projected vertical plane. | [9 empty] | 11 |  |  | 2 | 35 | 23.9 | 27.8 | 19.1 | 13.4 | -10.5 | 11.7 | -7.5 | -12.3 | -14 | 99
| Minimum wind load for C&C shall be 10 psf acting in either direction normal to surface. | [9 empty] | 1 |  | 0 | 1 | 33.4 | -17.3 | 22.1 | -10.3 | -40 | -22.7 | -27.9 | -17.6 | -56.1 | -43.9 | 100
11. | References: | [9 empty] | 2 |  | 5 | 1 | 33.4 | -17.3 | 22.1 | -10.3 | -40 | -22.7 | -27.9 | -17.6 | -56.1 | -43.9 | 101
| a. ASCE 7-05 Standard, "Minimum Design Loads for Buildings and Other Structures". | [9 empty] | 3 |  | 10 | 1 | 37.7 | -15.6 | 25 | -9.1 | -40 | -24.5 | -27.9 | -18.8 | -56.1 | -43.9 | 102 | 0
| b. "Guide to the Use of the Wind Load Provisions of ASCE 7-05" | [9 empty] | 4 |  | 15 | 1 | 41.8 | -13.8 | 27.9 | -7.9 | -40 | -26.2 | -27.9 | -20 | -56.1 | -43.9 | 103
| by: Kishor C. Mehta and William L. Coulbourne (2010). | [9 empty] | 5 |  | 20 | 1 | 46.1 | -12.2 | 30.8 | -6.8 | -40 | -27.9 | -27.9 | -21.1 | -56.1 | -43.9 | 104
[11 empty] | 6 | 145 | 25 | 1 | 41.8 | 6.8 | 30.3 | 6.9 | -18.6 | -25.3 | -13.4 | -20.4 | -34.6 | -29.5 | 105
[9 empty] | (continued) |  | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -7.1 | -13.7 | -1.9 | -8.8 | 0 | 0 | 106
[11 empty] | 8 |  | 30 | 1 | 37.5 | 25.6 | 29.8 | 20.5 | 2.9 | -22.7 | 1 | -19.5 | -13.2 | -15 | 107
[11 empty] | 9 |  |  | 2 | 35.7 | 25.6 | 29.8 | 20.5 | 14.4 | -11.3 | 12.6 | -8 | -13.2 | -15 | 108
[11 empty] | 10 |  | 45 | 1 | 37.5 | 25.6 | 29.8 | 20.5 | 2.9 | -22.7 | 1 | -19.5 | -13.2 | -15 | 109
[11 empty] | 11 |  |  | 2 | 35.7 | 25.6 | 29.8 | 20.5 | 14.4 | -11.3 | 12.6 | -8 | -13.2 | -15 | 110
[11 empty] | 1 |  | 0 | 1 | 35.7 | -18.5 | 23.7 | -11 | -42.9 | -24.4 | -29.8 | -18.9 | -60 | -47 | 111
[11 empty] | 2 |  | 5 | 1 | 35.7 | -18.5 | 23.7 | -11 | -42.9 | -24.4 | -29.8 | -18.9 | -60 | -47 | 112
[11 empty] | 3 |  | 10 | 1 | 40.2 | -16.7 | 26.8 | -9.7 | -42.9 | -26.2 | -29.8 | -20.1 | -60 | -47 | 113 | 0
[11 empty] | 4 |  | 15 | 1 | 44.8 | -14.9 | 29.8 | -8.5 | -42.9 | -28 | -29.8 | -21.4 | -60 | -47 | 114
[11 empty] | 5 |  | 20 | 1 | 49.4 | -13 | 32.9 | -7.2 | -42.9 | -29.8 | -29.8 | -22.6 | -60 | -47 | 115
[11 empty] | 6 | 150 | 25 | 1 | 44.8 | 7.2 | 32.4 | 7.4 | -19.9 | -27.1 | -14.4 | -21.6 | -37 | -31.6 | 116
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -7.5 | -14.7 | -2.1 | -9.4 | 0 | 0 | 117
[11 empty] | 8 |  | 30 | 1 | 40.1 | 27.4 | 31.9 | 22 | 3.1 | -24.4 | 1 | -20.9 | -14.1 | -16.1 | 118
[11 empty] | 9 |  |  | 2 | 40.1 | 27.4 | 31.9 | 22 | 15.4 | -12 | 13.4 | -8.6 | -14.1 | -16.1 | 119
[11 empty] | 10 |  | 45 | 1 | 40.1 | 27.4 | 31.9 | 22 | 3.1 | -24.4 | 1 | -20.9 | -14.1 | -16.1 | 120
[11 empty] | 11 |  |  | 2 | 40.1 | 27.4 | 31.9 | 22 | 15.4 | -12 | 13.4 | -8.6 | -14.1 | -16.1 | 121
[11 empty] | 1 |  | 0 | 1 | 45.8 | -23.8 | 30.4 | -14.1 | -55.1 | -31.3 | -38.3 | -24.2 | -77.1 | -60.4 | 122
[11 empty] | 2 |  | 5 | 1 | 45.8 | -23.8 | 30.4 | -14.1 | -55.1 | -31.3 | -38.3 | -24.2 | -77.1 | -60.4 | 123
[11 empty] | 3 |  | 10 | 1 | 51.7 | -21.4 | 34.4 | -12.5 | -55.1 | -33.6 | -38.3 | -25.8 | -77.1 | -60.4 | 124 | 0
[11 empty] | 4 |  | 15 | 1 | 57.6 | -19.1 | 38.3 | -10.9 | -55.1 | -36 | -38.3 | -27.5 | -77.1 | -60.4 | 125
[11 empty] | 5 |  | 20 | 1 | 63.4 | -16.7 | 42.3 | -9.3 | -55.1 | -38.3 | -38.3 | -29.1 | -77.1 | -60.4 | 126
[11 empty] | 6 | 170 | 25 | 1 | 57.5 | 9.3 | 41.6 | 9.5 | -25.6 | -34.8 | -18.5 | -28 | -47.6 | -40.5 | 127
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -9.7 | -18.9 | -2.6 | -12.1 | 0 | 0 | 128
[11 empty] | 8 |  | 30 | 1 | 51.5 | 35.2 | 41 | 28.2 | 4 | -31.3 | 1.3 | -26.9 | -18.1 | -20.7 | 129
[11 empty] | 9 |  |  | 2 | 51.5 | 35.2 | 41 | 28.2 | 19.8 | -15.4 | 17.2 | -11 | -18.1 | -20.7 | 130
|  |  | MWFRS - Wind Zones | [7 empty] | 10 |  | 45 | 1 | 51.5 | 35.2 | 41 | 28.2 | 4 | -31.3 | 1.3 | -26.9 | -18.1 | -20.7 | 131
[11 empty] | 11 |  |  | 2 | 51.5 | 35.2 | 41 | 28.2 | 19.8 | -15.4 | 17.2 | -11 | -18.1 | -20.7 | 132
[25 empty] | 14 | Select: | 5.5722 | 12.9945 | -6.6199 | 8.6259 | -3.9428 | -15.4 | -8.8687 | -10.7 | -6.8458 | -21.6 | -16.9
For Longitudinal Direction:
[12 empty] | Main Wind Force Resisting System - Method 1 |  |  |  |  | for h <= 60 ft.
[12 empty] | Figure 6-2 |  | Design Wind Pressures | [11 empty] | Select values from Figure 6-2 based on wind speed and roof angle:
[12 empty] | Enclosed Buildings |  |  |  |  | WALLS and ROOFS | [9 empty] | Use Roof Angle, q = | 0 | deg. | (assumed for longitudinal direction)
[12 empty] | Simplified Design Wind Pressure, ps30 (psf) (Exposure B at h = 30 ft. with Iw = 1.0) | [14 empty] | Mean Roof Ht., h = | 17 | ft. | h = (hr+he)/2 (assumed for longitudinal direction)
[12 empty] | Basic Wind | Roof | Load | Zones
[12 empty] | Speed, V | Angle | Case | Horizontal Pressures |  |  |  | Vertical Pressures |  |  |  | Overhangs
[11 empty] | Index | (mph) | (deg.) |  | A | B | C | D | E | F | G | H | Eoh | Goh | Index |  | q | A | B | C | D | E | F | G | H | Eoh | Goh
[11 empty] | 1 |  | 0 | 1 | 11.5 | -5.9 | 7.6 | -3.5 | -13.8 | -7.8 | -9.6 | -6.1 | -19.3 | -15.1 | 1
[11 empty] | 2 |  | 5 | 1 | 11.5 | -5.9 | 7.6 | -3.5 | -13.8 | -7.8 | -9.6 | -6.1 | -19.3 | -15.1 | 2
[11 empty] | 3 |  | 10 | 1 | 12.9 | -5.4 | 8.6 | -3.1 | -13.8 | -8.4 | -9.6 | -6.5 | -19.3 | -15.1 | 3 | 0
[11 empty] | 4 |  | 15 | 1 | 14.4 | -4.8 | 9.6 | -2.7 | -13.8 | -9 | -9.6 | -6.9 | -19.3 | -15.1 | 4
[11 empty] | 5 |  | 20 | 1 | 15.9 | -4.2 | 10.6 | -2.3 | -13.8 | -9.6 | -9.6 | -7.3 | -19.3 | -15.1 | 5
[11 empty] | 6 | 85 | 25 | 1 | 14.4 | 2.3 | 10.4 | 2.4 | -6.4 | -8.7 | -4.6 | -7 | -11.9 | -10.1 | 6
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -2.4 | -4.7 | -0.7 | -3 | 0 | 0 | 7
[11 empty] | 8 |  | 30 | 1 | 12.9 | 8.8 | 10.2 | 7 | 1 | -7.8 | 0.3 | -6.7 | -4.5 | -5.2 | 8
[11 empty] | 9 |  |  | 2 | 12.9 | 8.8 | 10.2 | 7 | 5 | -3.9 | 4.3 | -2.8 | -4.5 | -5.2 | 9
[11 empty] | 10 |  | 45 | 1 | 12.9 | 8.8 | 10.2 | 7 | 1 | -7.8 | 0.3 | -6.7 | -4.5 | -5.2 | 10
[11 empty] | 11 |  |  | 2 | 12.9 | 8.8 | 10.2 | 7 | 5 | -3.9 | 4.3 | -2.8 | -4.5 | -5.2 | 11
[11 empty] | 1 |  | 0 | 1 | 12.8 | -6.7 | 8.5 | -4 | -15.4 | -8.8 | -10.7 | -6.8 | -21.6 | -16.9 | 12 |  | 0 | 12.8 | -6.7 | 8.5 | -4 | -15.4 | -8.8 | -10.7 | -6.8 | -21.6 | -16.9
[11 empty] | 2 |  | 5 | 1 | 12.8 | -6.7 | 8.5 | -4 | -15.4 | -8.8 | -10.7 | -6.8 | -21.6 | -16.9 | 13 |  | 5 | 12.8 | -6.7 | 8.5 | -4 | -15.4 | -8.8 | -10.7 | -6.8 | -21.6 | -16.9
[11 empty] | 3 |  | 10 | 1 | 14.5 | -6 | 9.6 | -3.5 | -15.4 | -9.4 | -10.7 | -7.2 | -21.6 | -16.9 | 14 | 1 | 0 | 12.8 | -6.7 | 8.5 | -4 | -15.4 | -8.8 | -10.7 | -6.8 | -21.6 | -16.9
[11 empty] | 4 |  | 15 | 1 | 16.1 | -5.4 | 10.7 | -3 | -15.4 | -10.1 | -10.7 | -7.7 | -21.6 | -16.9 | 15
[11 empty] | 5 |  | 20 | 1 | 17.8 | -4.7 | 11.9 | -2.6 | -15.4 | -10.7 | -10.7 | -8.1 | -21.6 | -16.9 | 16
[11 empty] | 6 | 90 | 25 | 1 | 16.1 | 2.6 | 11.7 | 2.7 | -7.2 | -9.8 | -5.2 | -7.8 | -13.3 | -11.4 | 17
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -2.7 | -5.3 | -0.7 | -3.4 | 0 | 0 | 18
[11 empty] | 8 |  | 30 | 1 | 14.4 | 9.9 | 11.5 | 7.9 | 1.1 | -8.8 | 0.4 | -7.5 | -5.1 | -5.8 | 19
[11 empty] | 9 |  |  | 2 | 14.4 | 9.9 | 11.5 | 7.9 | 5.6 | -4.3 | 4.8 | -3.1 | -5.1 | -5.8 | 20
|  |  | Components and Cladding - Wind Zones | [7 empty] | 10 |  | 45 | 1 | 14.4 | 9.9 | 11.5 | 7.9 | 1.1 | -8.8 | 0.4 | -7.5 | -5.1 | -5.8 | 21
[11 empty] | 11 |  |  | 2 | 14.4 | 9.9 | 11.5 | 7.9 | 5.6 | -4.3 | 4.8 | -3.1 | -5.1 | -5.8 | 22
[11 empty] | 1 |  | 0 | 1 | 15.9 | -8.2 | 10.5 | -4.9 | -19.1 | -10.8 | -13.3 | -8.4 | -26.7 | -20.9 | 23
[11 empty] | 2 |  | 5 | 1 | 15.9 | -8.2 | 10.5 | -4.9 | -19.1 | -10.8 | -13.3 | -8.4 | -26.7 | -20.9 | 24
[11 empty] | 3 |  | 10 | 1 | 17.9 | -7.4 | 11.9 | -4.3 | -19.1 | -11.6 | -13.3 | -8.9 | -26.7 | -20.9 | 25 | 0
[11 empty] | 4 |  | 15 | 1 | 19.9 | -6.6 | 13.3 | -3.8 | -19.1 | -12.4 | -13.3 | -9.5 | -26.7 | -20.9 | 26
[11 empty] | 5 |  | 20 | 1 | 22 | -5.8 | 14.6 | -3.2 | -19.1 | -13.3 | -13.3 | -10.1 | -26.7 | -20.9 | 27
[11 empty] | 6 | 100 | 25 | 1 | 19.9 | 3.2 | 14.4 | 3.3 | -8.8 | -12 | -6.4 | -9.7 | -16.5 | -14 | 28
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -3.4 | -6.6 | -0.9 | -4.2 | 0 | 0 | 29
[11 empty] | 8 |  | 30 | 1 | 17.8 | 12.2 | 14.2 | 9.8 | 1.4 | -10.8 | 0.5 | -9.3 | -6.3 | -7.2 | 30
[11 empty] | 9 |  |  | 2 | 17.8 | 12.2 | 14.2 | 9.8 | 6.9 | -5.3 | 5.9 | -3.8 | -6.3 | -7.2 | 31
[11 empty] | 10 |  | 45 | 1 | 17.8 | 12.2 | 14.2 | 9.8 | 1.4 | -10.8 | 0.5 | -9.3 | -6.3 | -7.2 | 32
[11 empty] | 11 |  |  | 2 | 17.8 | 12.2 | 14.2 | 9.8 | 6.9 | -5.3 | 5.9 | -3.8 | -6.3 | -7.2 | 33
[11 empty] | 1 |  | 0 | 1 | 17.5 | -9 | 11.6 | -5.4 | -21.1 | -11.9 | -14.7 | -9.3 | -29.4 | -23 | 34
[11 empty] | 2 |  | 5 | 1 | 17.5 | -9 | 11.6 | -5.4 | -21.1 | -11.9 | -14.7 | -9.3 | -29.4 | -23 | 35
[11 empty] | 3 |  | 10 | 1 | 19.7 | -8.2 | 13.1 | -4.7 | -21.1 | -12.8 | -14.7 | -9.8 | -29.4 | -23 | 36 | 0
[11 empty] | 4 |  | 15 | 1 | 21.9 | -7.3 | 14.7 | -4.2 | -21.1 | -13.7 | -14.7 | -10.5 | -29.4 | -23 | 37
[11 empty] | 5 |  | 20 | 1 | 24.3 | -8.4 | 16.1 | -3.5 | -21.1 | -14.7 | -14.7 | -11.1 | -29.4 | -23 | 38
[11 empty] | 6 | 105 | 25 | 1 | 21.9 | 3.5 | 15.9 | 3.5 | -9.7 | -7.1 | -7.1 | -10.7 | -18.2 | -15.4 | 39
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -3.7 | -1 | -1 | -4.6 | 0 | 0 | 40
[11 empty] | 8 |  | 30 | 1 | 19.6 | 13.5 | 10.8 | 10.8 | 1.5 | 0.6 | 0.6 | -10.3 | -6.9 | -7.9 | 41
[11 empty] | 9 |  |  | 2 | 19.6 | 13.5 | 10.8 | 10.8 | 7.6 | 6.5 | 6.5 | -4.2 | -6.9 | -7.9 | 42
[11 empty] | 10 |  | 45 | 1 | 19.6 | 13.5 | 10.8 | 10.8 | 1.5 | 0.6 | 0.6 | -10.3 | -6.9 | -7.9 | 43
[11 empty] | 11 |  |  | 2 | 19.6 | 13.5 | 10.8 | 10.8 | 7.6 | 6.5 | 6.5 | -4.2 | -6.9 | -7.9 | 44
[11 empty] | 1 |  | 0 | 1 | 19.2 | -10 | 12.7 | -5.9 | -23.1 | -13.1 | -16 | -10.1 | -32.3 | -25.3 | 45
[11 empty] | 2 |  | 5 | 1 | 19.2 | -10 | 12.7 | -5.9 | -23.1 | -13.1 | -16 | -10.1 | -32.3 | -25.3 | 46
[11 empty] | 3 |  | 10 | 1 | 21.6 | -9 | 14.4 | -5.2 | -23.1 | -14.1 | -16 | -10.8 | -32.3 | -25.3 | 47 | 0
[11 empty] | 4 |  | 15 | 1 | 24.1 | -8 | 16 | -4.6 | -23.1 | -15.1 | -16 | -11.5 | -32.3 | -25.3 | 48
[11 empty] | 5 |  | 20 | 1 | 26.6 | -7 | 17.7 | -3.9 | -23.1 | -16 | -16 | -12.2 | -32.3 | -25.3 | 49
[11 empty] | 6 | 110 | 25 | 1 | 24.1 | 3.9 | 17.4 | 4 | -10.7 | -14.6 | -7.7 | -11.7 | -19.9 | -17 | 50
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -4.1 | -7.9 | -1.1 | -5.1 | 0 | 0 | 51
[11 empty] | 8 |  | 30 | 1 | 21.6 | 14.8 | 17.2 | 11.8 | 1.7 | -13.1 | 0.6 | -11.3 | -7.6 | -8.7 | 52
[11 empty] | 9 |  |  | 2 | 21.6 | 14.8 | 17.2 | 11.8 | 8.3 | -6.5 | 7.2 | -4.6 | -7.6 | -8.7 | 53
[11 empty] | 10 |  | 45 | 1 | 21.6 | 14.8 | 17.2 | 11.8 | 1.7 | -13.1 | 0.6 | -11.3 | -7.6 | -8.7 | 54
[11 empty] | 11 |  |  | 2 | 21.6 | 14.8 | 17.2 | 11.8 | 8.3 | -6.5 | 7.2 | -4.6 | -7.6 | -8.7 | 55
[11 empty] | 1 |  | 0 | 1 | 22.8 | -11.9 | 15.1 | -7 | -27.4 | -15.6 | -19.1 | -12.1 | -38.4 | -30.1 | 56
[11 empty] | 2 |  | 5 | 1 | 22.8 | -11.9 | 15.1 | -7 | -27.4 | -15.6 | -19.1 | -12.1 | -38.4 | -30.1 | 57
[11 empty] | 3 |  | 10 | 1 | 25.8 | -10.7 | 17.1 | -6.2 | -27.4 | -16.8 | -19.1 | -12.9 | -38.4 | -30.1 | 58 | 0
[11 empty] | 4 |  | 15 | 1 | 29.7 | -9.5 | 19.1 | -5.4 | -27.4 | -17.9 | -19.1 | -13.7 | -38.4 | -30.1 | 59
[11 empty] | 5 |  | 20 | 1 | 31.6 | -8.3 | 21.1 | -4.6 | -27.4 | -19.1 | -19.1 | -14.5 | -38.4 | -30.1 | 60
[11 empty] | 6 | 120 | 25 | 1 | 28.6 | 4.6 | 20.7 | 4.7 | -12.7 | -17.3 | -9.2 | -13.9 | -23.7 | -20.2 | 61
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -4.8 | -9.4 | -1.3 | -6 | 0 | 0 | 62
[11 empty] | 8 |  | 30 | 1 | 25.7 | 17.6 | 20.4 | 14 | 2 | -15.6 | 0.7 | -13.4 | -9 | -10.3 | 63
[11 empty] | 9 |  |  | 2 | 25.7 | 17.6 | 20.4 | 14 | 9.9 | -7.7 | 8.6 | -5.5 | -9 | -10.3 | 64
[11 empty] | 10 |  | 45 | 1 | 25.7 | 17.6 | 20.4 | 14 | 2 | -15.6 | 0.7 | -13.4 | -9 | -10.3 | 65
[11 empty] | 11 |  |  | 2 | 25.7 | 17.6 | 20.4 | 14 | 9.9 | -7.7 | 8.6 | -5.5 | -9 | -10.3 | 66
[11 empty] | 1 |  | 0 | 1 | 24.7 | -12.9 | 16.4 | -7.6 | -29.7 | -16.9 | -20.7 | -13.1 | -41.7 | -32.7 | 67
[11 empty] | 2 |  | 5 | 1 | 24.7 | -12.9 | 16.4 | -7.6 | -29.7 | -16.9 | -20.7 | -13.1 | -41.7 | -32.7 | 68
[11 empty] | 3 |  | 10 | 1 | 28 | -11.6 | 18.6 | -6.7 | -29.7 | -18.2 | -20.7 | -14 | -41.7 | -32.7 | 69 | 0
[11 empty] | 4 |  | 15 | 1 | 31.1 | -10.3 | 20.7 | -5.9 | -29.7 | -19.4 | -20.7 | -14.9 | -41.7 | -32.7 | 70
[11 empty] | 5 |  | 20 | 1 | 34.3 | -9 | 22.9 | -5 | -29.7 | -20.7 | -20.7 | -15.7 | -41.7 | -32.7 | 71
[11 empty] | 6 | 125 | 25 | 1 | 31 | 5 | 22.5 | 5.1 | -13.8 | -18.8 | -10 | -15.1 | -25.7 | -21.9 | 72
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -5.2 | -10.2 | -1.4 | -6.5 | 0 | 0 | 73
[11 empty] | 8 |  | 30 | 1 | 27.9 | 19.1 | 22.1 | 15.2 | 2.2 | -16.9 | 0.8 | -14.5 | -9.8 | -11.2 | 74
[11 empty] | 9 |  |  | 2 | 27.9 | 19.1 | 22.1 | 15.2 | 10.7 | -8.4 | 9.3 | -6 | -9.8 | -11.2 | 75
[11 empty] | 10 |  | 45 | 1 | 27.9 | 19.1 | 22.1 | 15.2 | 2.2 | -16.9 | 0.8 | -14.5 | -9.8 | -11.2 | 76
[11 empty] | 11 |  |  | 2 | 27.9 | 19.1 | 22.1 | 15.2 | 10.7 | -8.4 | 9.3 | -6 | -9.8 | -11.2 | 77
[11 empty] | 1 |  | 0 | 1 | 26.8 | -13.9 | 17.8 | -8.2 | -32.2 | -18.3 | -22.4 | -14.2 | -45.1 | -35.3 | 78
[11 empty] | 2 |  | 5 | 1 | 26.8 | -13.9 | 17.8 | -8.2 | -32.2 | -18.3 | -22.4 | -14.2 | -45.1 | -35.3 | 79
[11 empty] | 3 |  | 10 | 1 | 30.2 | -12.5 | 20.1 | -7.3 | -32.2 | -19.7 | -22.4 | -15.1 | -45.1 | -35.3 | 80 | 0
[11 empty] | 4 |  | 15 | 1 | 33.7 | -11.2 | 22.4 | -6.4 | -32.2 | -21 | -22.4 | -16.1 | -45.1 | -35.3 | 81
[11 empty] | 5 |  | 20 | 1 | 37.1 | -9.8 | 24.7 | -5.4 | -32.2 | -22.4 | -22.4 | -17 | -45.1 | -35.3 | 82
[11 empty] | 6 | 130 | 25 | 1 | 33.6 | 5.4 | 24.3 | 5.5 | -14.9 | -20.4 | -10.8 | -16.4 | -27.8 | -23.7 | 83
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -5.7 | -11.1 | -1.5 | -7.1 | 0 | 0 | 84
[11 empty] | 8 |  | 30 | 1 | 30.1 | 20.6 | 24 | 16.5 | 2.3 | -18.3 | 0.8 | -15.7 | -10.6 | -12.1 | 85
[11 empty] | 9 |  |  | 2 | 30.1 | 20.6 | 24 | 16.5 | 11.6 | -9 | 10 | -6.4 | -10.6 | -12.1 | 86
[11 empty] | 10 |  | 45 | 1 | 30.1 | 20.6 | 24 | 16.5 | 2.3 | -18.3 | 0.8 | -15.7 | -10.6 | -12.1 | 87
[11 empty] | 11 |  |  | 2 | 30.1 | 20.6 | 24 | 16.5 | 11.6 | -9 | 10 | -6.4 | -10.6 | -12.1 | 88
[11 empty] | 1 |  | 0 | 1 | 31.1 | -16.1 | 20.6 | -9.6 | -37.3 | -21.2 | -26 | -16.4 | -52.3 | -40.9 | 89
[11 empty] | 2 |  | 5 | 1 | 31.1 | -16.1 | 20.6 | -9.6 | -37.3 | -21.2 | -26 | -16.4 | -52.3 | -40.9 | 90
[11 empty] | 3 |  | 10 | 1 | 35.1 | -14.5 | 23.3 | -8.5 | -37.3 | -22.8 | -26 | -17.5 | -52.3 | -40.9 | 91 | 0
[11 empty] | 4 |  | 15 | 1 | 39 | -12.9 | 26 | -7.4 | -37.3 | -24.4 | -26 | -18.6 | -52.3 | -40.9 | 92
[11 empty] | 5 |  | 20 | 1 | 43 | -11.4 | 28.7 | -6.3 | -37.3 | -26 | -26 | -19.7 | -52.3 | -40.9 | 92
[11 empty] | 6 | 140 | 25 | 1 | 39 | 6.3 | 28.2 | 6.4 | -17.3 | -23.6 | -12.5 | -19 | -32.3 | -27.5 | 94
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -6.6 | -12.8 | -1.8 | -8.2 | 0 | 0 | 95
[11 empty] | 8 |  | 30 | 1 | 35 | 23.9 | 27.8 | 19.1 | 2.7 | -21.2 | 0.9 | -18.2 | -12.3 | -14 | 96
[11 empty] | 9 |  |  | 2 | 35 | 23.9 | 27.8 | 19.1 | 13.4 | -10.5 | 11.7 | -7.5 | -12.3 | -14 | 97
[11 empty] | 10 |  | 45 | 1 | 35 | 23.9 | 27.8 | 19.1 | 2.7 | -21.2 | 0.9 | -18.2 | -12.3 | -14 | 98
[11 empty] | 11 |  |  | 2 | 35 | 23.9 | 27.8 | 19.1 | 13.4 | -10.5 | 11.7 | -7.5 | -12.3 | -14 | 99
[11 empty] | 1 |  | 0 | 1 | 33.4 | -17.3 | 22.1 | -10.3 | -40 | -22.7 | -27.9 | -17.6 | -56.1 | -43.9 | 100
[11 empty] | 2 |  | 5 | 1 | 33.4 | -17.3 | 22.1 | -10.3 | -40 | -22.7 | -27.9 | -17.6 | -56.1 | -43.9 | 101
[11 empty] | 3 |  | 10 | 1 | 37.7 | -15.6 | 25 | -9.1 | -40 | -24.5 | -27.9 | -18.8 | -56.1 | -43.9 | 102 | 0
[11 empty] | 4 |  | 15 | 1 | 41.8 | -13.8 | 27.9 | -7.9 | -40 | -26.2 | -27.9 | -20 | -56.1 | -43.9 | 103
[11 empty] | 5 |  | 20 | 1 | 46.1 | -12.2 | 30.8 | -6.8 | -40 | -27.9 | -27.9 | -21.1 | -56.1 | -43.9 | 104
[11 empty] | 6 | 145 | 25 | 1 | 41.8 | 6.8 | 30.3 | 6.9 | -18.6 | -25.3 | -13.4 | -20.4 | -34.6 | -29.5 | 105
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -7.1 | -13.7 | -1.9 | -8.8 | 0 | 0 | 106
[11 empty] | 8 |  | 30 | 1 | 37.5 | 25.6 | 29.8 | 20.5 | 2.9 | -22.7 | 1 | -19.5 | -13.2 | -15 | 107
[11 empty] | 9 |  |  | 2 | 35.7 | 25.6 | 29.8 | 20.5 | 14.4 | -11.3 | 12.6 | -8 | -13.2 | -15 | 108
[11 empty] | 10 |  | 45 | 1 | 37.5 | 25.6 | 29.8 | 20.5 | 2.9 | -22.7 | 1 | -19.5 | -13.2 | -15 | 109
[11 empty] | 11 |  |  | 2 | 35.7 | 25.6 | 29.8 | 20.5 | 14.4 | -11.3 | 12.6 | -8 | -13.2 | -15 | 110
[11 empty] | 1 |  | 0 | 1 | 35.7 | -18.5 | 23.7 | -11 | -42.9 | -24.4 | -29.8 | -18.9 | -60 | -47 | 111
[11 empty] | 2 |  | 5 | 1 | 35.7 | -18.5 | 23.7 | -11 | -42.9 | -24.4 | -29.8 | -18.9 | -60 | -47 | 112
[11 empty] | 3 |  | 10 | 1 | 40.2 | -16.7 | 26.8 | -9.7 | -42.9 | -26.2 | -29.8 | -20.1 | -60 | -47 | 113 | 0
[11 empty] | 4 |  | 15 | 1 | 44.8 | -14.9 | 29.8 | -8.5 | -42.9 | -28 | -29.8 | -21.4 | -60 | -47 | 114
[11 empty] | 5 |  | 20 | 1 | 49.4 | -13 | 32.9 | -7.2 | -42.9 | -29.8 | -29.8 | -22.6 | -60 | -47 | 115
[11 empty] | 6 | 150 | 25 | 1 | 44.8 | 7.2 | 32.4 | 7.4 | -19.9 | -27.1 | -14.4 | -21.6 | -37 | -31.6 | 116
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -7.5 | -14.7 | -2.1 | -9.4 | 0 | 0 | 117
[11 empty] | 8 |  | 30 | 1 | 40.1 | 27.4 | 31.9 | 22 | 3.1 | -24.4 | 1 | -20.9 | -14.1 | -16.1 | 118
[11 empty] | 9 |  |  | 2 | 40.1 | 27.4 | 31.9 | 22 | 15.4 | -12 | 13.4 | -8.6 | -14.1 | -16.1 | 119
[11 empty] | 10 |  | 45 | 1 | 40.1 | 27.4 | 31.9 | 22 | 3.1 | -24.4 | 1 | -20.9 | -14.1 | -16.1 | 120
[11 empty] | 11 |  |  | 2 | 40.1 | 27.4 | 31.9 | 22 | 15.4 | -12 | 13.4 | -8.6 | -14.1 | -16.1 | 121
[11 empty] | 1 |  | 0 | 1 | 45.8 | -23.8 | 30.4 | -14.1 | -55.1 | -31.3 | -38.3 | -24.2 | -77.1 | -60.4 | 122
[11 empty] | 2 |  | 5 | 1 | 45.8 | -23.8 | 30.4 | -14.1 | -55.1 | -31.3 | -38.3 | -24.2 | -77.1 | -60.4 | 123
[11 empty] | 3 |  | 10 | 1 | 51.7 | -21.4 | 34.4 | -12.5 | -55.1 | -33.6 | -38.3 | -25.8 | -77.1 | -60.4 | 124 | 0
[11 empty] | 4 |  | 15 | 1 | 57.6 | -19.1 | 38.3 | -10.9 | -55.1 | -36 | -38.3 | -27.5 | -77.1 | -60.4 | 125
[11 empty] | 5 |  | 20 | 1 | 63.4 | -16.7 | 42.3 | -9.3 | -55.1 | -38.3 | -38.3 | -29.1 | -77.1 | -60.4 | 126
[11 empty] | 6 | 170 | 25 | 1 | 57.5 | 9.3 | 41.6 | 9.5 | -25.6 | -34.8 | -18.5 | -28 | -47.6 | -40.5 | 127
[11 empty] | 7 |  |  | 2 | 0 | 0 | 0 | 0 | -9.7 | -18.9 | -2.6 | -12.1 | 0 | 0 | 128
[11 empty] | 8 |  | 30 | 1 | 51.5 | 35.2 | 41 | 28.2 | 4 | -31.3 | 1.3 | -26.9 | -18.1 | -20.7 | 129
[11 empty] | 9 |  |  | 2 | 51.5 | 35.2 | 41 | 28.2 | 19.8 | -15.4 | 17.2 | -11 | -18.1 | -20.7 | 130
[11 empty] | 10 |  | 45 | 1 | 51.5 | 35.2 | 41 | 28.2 | 4 | -31.3 | 1.3 | -26.9 | -18.1 | -20.7 | 131
[11 empty] | 11 |  |  | 2 | 51.5 | 35.2 | 41 | 28.2 | 19.8 | -15.4 | 17.2 | -11 | -18.1 | -20.7 | 132
[25 empty] | 14 | Select: | 0 | 12.8 | -6.7 | 8.5 | -4 | -15.4 | -8.8 | -10.7 | -6.8 | -21.6 | -16.9
[12 empty] | Adjustment Factor |  |  |  |  | Determine End Zone Width 'a' (Figures 6-2 and 6-3):
[12 empty] | for Building Height and Exposure, l | [5 empty] | Lesser of L or W: | 41 | ft.
[11 empty] | Index | Height, h (ft.) | B | C | D |  |  | 0.1*(L or W): | 4.1 | ft.
[11 empty] | 1 | 15 | 1 | 1.21 | 1.47 |  |  | Compare to 0.4*h: | 4.1 | ft.
[11 empty] | 2 | 20 | 1 | 1.29 | 1.55 |  |  | Compare to .04*(L,W): | 4.1 | ft.
[11 empty] | 3 | 25 | 1 | 1.35 | 1.61 |  |  | Compare to 3': | 4.1 | ft.
[11 empty] | 4 | 30 | 1 | 1.4 | 1.66 |  |  | Use 'a' = | 4.1 | ft.
[11 empty] | 5 | 35 | 1.05 | 1.45 | 1.7
[11 empty] | 6 | 40 | 1.09 | 1.49 | 1.74
[11 empty] | 7 | 45 | 1.12 | 1.53 | 1.78
[11 empty] | 8 | 50 | 1.26 | 1.56 | 1.81
[11 empty] | 9 | 55 | 1.19 | 1.59 | 1.84
[11 empty] | 10 | 60 | 1.22 | 1.62 | 1.87
[12 empty] | h | B | C | D
[12 empty] | 15 | 1 | 1.21 | 1.47
[12 empty] | 20 | 1 | 1.29 | 1.55
[12 empty] | 17 | 1 | 1.242 | 1.502
[12 empty] | Use: l = | 1
Note on C8: The Basic Design Wind Speed, V (mph), corresponds to a 3-second gust speed at 33' above ground in Exposure Category "C" and is associated with an annual probability of 0.02 of being equaled or exceeded (50-year mean recurrence interval). For Basic Wind Speed Map (Fig. 6-1) see 'Wind Map' worksheet of this workbook.
Note on C9: TABLE 1-1 Occupancy Category of Buildings and Other Structures for Flood, Wind, Snow, Earthquake, and Ice Loads Nature of Occupancy Occupancy Category Buildings and structures that represent a low hazard to human life in the event of failure including, I but not limited to: - Agriculture facilities - Certain temporary facilities - Minor storage facilities Buildings and other structures except those listed in Categories I, III and IV II Buildings and other structures that represent a substantial hazard to human life in the event of III failure including, but not limited to: - Buildings and other structures where more than 300 people congregate in one area - Buildings and other structures with day-care facilities with capacity greater than 150 - Elementary or secondary school facilities with capacity greater than 250 - Colleges & adult education facilities with a capacity greater than 500 - Health care facilities with a capacity greater than 50 resident patients but not having surgery or emergency treatment facilities - Jails and detention facilities Buildings and other structures, not includes in Occupancy Category IV, with potential to cause substantial economic impact and/or mass disruption of day-to-day civilian life in event of failure, including, but not limited to: - Power generating stations, water treatment facilities, sewage treatment facilities, and telecommunication centers - Buildings and structures not included in Category IV containing sufficient quantities of toxic, explosive, or other hazardous materials dangerous to the public if released Buildings and other structures designated as essential facilities including, but not limited to: IV - Hospitals and health care facilities having surgery or emergency treatment facilities - Fire, rescue and police stations and emergency vehicle garages - Designated earthquake, hurricane or other emergency shelters - Designated emergency preparedness, communication, and operation centers and other facilities required for emergency response - Power-generating stations and other public utility facilities required in an emergency - Ancillary structures required for operation of Category IV structures during an emergency - Aviation control towers, air traffic control centers and emergency aircraft hangars - Water storage facilities and pump structures required to maintain water pressure for fire suppression - Buildings and other structures having critical national defense functions - Buildings and structures containing extremely hazardous materials where quantity of material exceeds a threshold quantity established by authority having jurisdiction
Note on C10: Surface Roughness Categories for the purpose of assigning Exposure Category are defined as follows: Surface Roughness "B": Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single family dwellings or larger. Surface Roughness "C": Open terrain with scattered obstructions having heights generally < 30 ft. This category includes flat open country, grass lands, and all water surfaces in hurricane prone regions. Surface Roughness "D": Flat, unobstructed areas and water surfaces outside hurricane prone regions. This category includes smooth mud flats, salt flats, and unbroken ice. Exposure Categories are defined as follows: Exposure "B": Exposure B shall apply where the ground surface roughness condition, as defined by Surface Roughness B, prevails in the upwind direction for a distance of at least 2600 ft. or 20 times the building height, whichever is greater. Exception: For buildings whose mean roof height <= 30 ft., the upwind distance may be reduced to 1500 ft. Exposure "C": Exposure C shall apply for all cases where exposures B and D do not apply. Exposure "D": Exposure D shall apply where the ground surface roughness, as defined by Surface Roughness D, prevails in the upwind direction for a distance >= 5,000 ft. or 20 times the building height, whichever is greater. Exposure D shall extend into downwind areas of Surface Roughness B or C for a distance of 600 ft. or 20 times the height of the building, whichever is greater.
Note on C12: The eave height, 'he', is the distance from the ground surface adjacent to the building to the roof eave line at a particular wall. If the height of the eave varies along the wall, the average height shall be used.
Note on C15: This program assumes that a Gable roof is symmetrical, as the ridge line is assumed in the center of the building width. For flat roofs (roof angle = 0 degrees), either Gable or Monoslope may be used.
Note on C16: The Topographic Factor, Kzt, accounts for effect of wind speed-up over isolated hills and escarpments (Sect. 6.5.7 and Fig. 6-4). Kzt = (1+K1*K2*K3)^2 (Eq. 6-3), where: H = height of hill or escarpment relative to the upwind terrain, in feet. Lh = Distance upwind of crest to where the difference in ground elevation is half the height of hill or escarpment, in feet. K1 = factor to account for shape of topographic feature and maximum speed-up effect. K2 = factor to account for reduction in speed-up with distance upwind or downwind of crest. K3 = factor to account for reduction in speed-up with height above local terrain. x = distance (upwind or downwind) from the crest to the building site, in feet. z = height above local ground level, in feet. The effect of wind speed-up shall not be required to be considered (Kzt = 1.0) when H/Lh < 0.2, or H < 15' for Exposures 'C' and 'D', or H < 60' for Exposure 'B'.
Note on C18: The Effective Area, for a component or cladding panel equals the span length times the effective width that need not be less than 1/3 of the span length; however, for a fastener it is the area tributary to an individual fastener. Note: Major structural components supporting tributary areas > 700 sq ft shall be permitted to be designed using the provisions for main wind-force resisting systems (MWFRS).
Note on C20: The Effective Area, for a component or cladding panel equals the span length times the effective width that need not be less than 1/3 of the span length; however, for a fastener it is the area tributary to an individual fastener. Note: Major structural components supporting tributary areas > 700 sq ft shall be permitted to be designed using the provisions for main wind-force resisting systems (MWFRS).
Note on C21: The Effective Area, for a component or cladding panel equals the span length times the effective width that need not be less than 1/3 of the span length; however, for a fastener it is the area tributary to an individual fastener. Note: Major structural components supporting tributary areas > 700 sq ft shall be permitted to be designed using the provisions for main wind-force resisting systems (MWFRS).
Note on D27: For buildings with roof angle <= 10 degrees: h = he (per Sect. 6-3).
Note on D28: Adjustment Factor for Building Height and Exposure, l Mean Roof Exposure Height (ft.) B C D 15 1.00 1.21 1.47 20 1.00 1.29 1.55 25 1.00 1.35 1.61 30 1.00 1.40 1.66 35 1.05 1.45 1.70 40 1.09 1.49 1.74 45 1.12 1.53 1.78 50 1.16 1.56 1.81 55 1.19 1.59 1.84 60 1.22 1.62 1.87
Note on D29: Importance Factor, I (Table 6-1): Non-Hurricane Prone Regions Hurricane Prone Regions Category and Hurricane Prone Regions with V > 100 mph with V = 85-100 mph and Alaska I 0.87 0.77 II 1.00 1.00 III 1.15 1.15 IV 1.15 1.15 Note: in the U.S. and its territories hurricane prone regions are defined as: 1. U.S. Atlantic Ocean and Gulf of Mexico coasts where the basic wind speed is > 90 mph. 2. Hawaii, Puerto Rico, Guam, Virgin Islands, and American Samoa.
Note on D30: Width 'a' is equal to 10% of least horizontal dimension or 0.4*h, whichever is smaller, but not less than either 4% of least horizontal dimension or 3'.
Note on D44: For wind in longitudinal direction, use q = 0 degrees (assumed).
Note on D45: For wind in longitudinal direction, h = he+(hr-he)/2
Note on D46: Adjustment Factor for Building Height and Exposure, l Mean Roof Exposure Height (ft.) B C D 15 1.00 1.21 1.47 20 1.00 1.29 1.55 25 1.00 1.35 1.61 30 1.00 1.40 1.66 35 1.05 1.45 1.70 40 1.09 1.49 1.74 45 1.12 1.53 1.78 50 1.16 1.56 1.81 55 1.19 1.59 1.84 60 1.22 1.62 1.87
Note on G60: The total design MWFRS load is assumed to be the total wind load on either the "Width" (W) or the "Length" (L) of the building respectively. A typical assumption might be that 1/2 of the total load goes to the roof while the other 1/2 goes to the base. Note: this design load represents the sum of both the windward and leeward walls.
Note on H32: ps = l*Kzt*I*ps30 where: ps30 is taken from Figure 6-2
Note on H33: Both load cases 1 and 2 are to be checked for roof angle, 25 degrees < q <= 45 degrees.
Note on H48: ps = l*Kzt*I*ps30 where: ps30 is taken from Figure 6-2
Note on H49: Both load cases 1 and 2 are to be checked for roof angle, 25 degrees < q <= 45 degrees.
Note on H70: ps = l*Kzt*I*pnet30 where: pnet30 is taken from Figure 6-3
Note on J3: For Method 1: Simplified Procedure (Sect. 6.4) to be used for an enclosed low-rise building to determine the design wind loads, all of the following nine conditions must be met: 1. The building is a simple diaphragm building, in which wind loads are transmitted through floor and roof diaphragms to the vertical Main Wind-Force Resisting System (MWFRS). 2. The building is a low-rise building where mean roof height, h <= 60 ft., and h <= least horizontal dimension, L or B. 3. The building is enclosed and conforms to wind-borne debris provisions. 4. The building is a regular shaped building, having no unusual geometrical irregularity in spatial form. 5. The building is not classified as a flexible building so it is considered "rigid". 6. The building does not have response characteristics making it subject to across-wind loading, vortex shedding, etc. 7. The building has an approximately symmetrical cross section in each direction with either a flat roof, or gable roof with q <= 45 degrees. 8. The building is exempted from torsional load cases or torsional load cases do not control any of the MWFRSs of the building.
Note on CW1: "ASCE705W.xls" written by: Alex Tomanovich, P.E.
q o
W
L
hr
he
h<=60'
W

## MWFRS (Low-Rise)
WIND LOADING ANALYSIS - Main Wind-Force Resisting System | [8 empty] | CALCULATIONS: | [5 empty] | Version 1.4
Per ASCE 7-05 Code for Enclosed or Partially Enclosed Buildings
Using Method 2: Analytical Procedure (Section 6.5) for Low-Rise Buildings | [7 empty] | I | Check 'Low-Rise' Criteria: |  |  |  | Roof Angle, q = | 18.4332
Job Name: |  |  |  | Subject: |  |  |  | II | Is h <= 60'? | Yes |  |  | Mean Roof Ht., h = | 36.665
Job Number: |  |  |  | Originator: |  | Checker: |  | III | Is h <= Lesser L,B? | Yes |  |  | Lesser of L or B = | 200
IV
Input Data: | [7 empty] | B | External Pressure Coefficients, GCpf (Fig. 6-10): |  |  | External Pressure Coefficients, GCpf (Fig. 6-10):
[8 empty] | C | For Transverse Case: |  |  | For Longitudinal Case:
Wind Speed, V = | 90 | mph (Wind Map, Figure 6-1) | [5 empty] | D | Wall Zone 1 = | 0.51642 |  | Wall Zone 1 = | 0.4
Bldg. Classification = | II | (Table 1-1 Occupancy Cat.) | [5 empty] | Gable | Roof Zone 2 = | -0.69 |  | Roof Zone 2 = | -0.69
Exposure Category = | C | (Sect. 6.5.6) | [5 empty] | Monoslope | Roof Zone 3 = | -0.46851 |  | Roof Zone 3 = | -0.37
Ridge Height, hr = | 53.33 | ft. (hr >= he) | [5 empty] | Y | Wall Zone 4 = | -0.41538 |  | Wall Zone 4 = | -0.29
Eave Height, he = | 20 | ft. (he <= hr) | [5 empty] | N | Wall Zone 5 = | -0.45 |  | Wall Zone 5 = | -0.45
Building Width = | 200 | ft. (Normal to Building Ridge) | [6 empty] | Wall Zone 6 = | -0.45 |  | Wall Zone 6 = | -0.45
Building Length = | 250 | ft. (Parallel to Building Ridge) | [6 empty] | Wall Zone 1E = | 0.78015 |  | Wall Zone 1E = | 0.61
Roof Type = | Gable | (Gable or Monoslope) | [6 empty] | Roof Zone 2E = | -1.07 |  | Roof Zone 2E = | -1.07
Topo. Factor, Kzt = | 1 | (Sect. 6.5.7 & Figure 6-4) | [6 empty] | Roof Zone 3E = | -0.67329 |  | Roof Zone 3E = | -0.53
Direct. Factor, Kd = | 0.85 | (Table 6-4) | [6 empty] | Wall Zone 4E = | -0.61807 |  | Wall Zone 4E = | -0.43
Enclosed? (Y/N) | Y | (Sect. 6.2 & Figure 6-5)
Hurricane Region? | Y | [7 empty] | Length of Roof Zones 2/2E for Transverse and Long. Cases when GCpf is Negative in Roof Zones 2/2E:
[9 empty] | For Transverse Case: |  |  | For Longitudinal Case:
Resulting Parameters and Coefficients: | [8 empty] | 0.5*L = | 100 |  | 0.5*B = | 125
[9 empty] | 2.5*he = | 50 |  | 2.5*he = | 50
Roof Angle, q = | 18.4332 | deg. | [6 empty] | Use = | 50 |  | Use = | 50
Mean Roof Ht., h = | 36.665 | ft. (h = (hr+he)/2, for angle >10 deg.)
Determine End Zone Widths 'a' and '2*a' (Fig. 6-10):
Check Criteria for a Low-Rise Building: | [9 empty] | Lesser of L or B: | 200
1. Is h <= 60' ? | Yes, O.K. |  | 2. Is h <= Lesser of L or B? |  |  | Yes, O.K. |  |  |  | 0.1*(L or B): | 20
[10 empty] | Compare to 0.4*h: | 14.666
External Pressure Coeff's., GCpf (Fig. 6-10): | [9 empty] | Compare to .04*(L, B): | 14.666
(For values, see following wind load tabulations.) | [9 empty] | Compare to 3': | 14.666
Positive & Negative Internal Pressure Coefficients, GCpi (Figure 6-5): | [9 empty] | Use 'a' = | 14.666
+GCpi Coef. = | 0.18 | (positive internal pressure) | [7 empty] | Use '2*a' = | 29.332
-GCpi Coef. = | -0.18 | (negative internal pressure)
Positive & Negative Internal Pressure Coefficients, GCpi (Figure 6-5):
If h < 15 then: Kh = 2.01*(15/zg)^(2/a) (Table 6-3, Case 1b) | [8 empty] | +GCpi Coef. (PIP) = | 0.18
If h >= 15 then: Kh = 2.01*(z/zg)^(2/a) (Table 6-3, Case 1b) | [8 empty] | -GCpi Coef. (NIP) = | -0.18
a = | 9.5 | (Table 6-2)
zg = | 900 | (Table 6-2) | [6 empty] | Determine a, zg, Kh, I, and qh:
Kh = | 1.0246 | (Kh = Kz evaluated at z = h) | [6 empty] | a = | 9.5 | (Table 6-2)
I = | 1 | (Table 6-1) | (Importance factor) | [5 empty] | zg = | 900 | (Table 6-2)
[9 empty] | Kh = | 1.0246 | (Table 6-3, Case 1b)
Velocity Pressure: qz = 0.00256*Kz*Kzt*Kd*V^2*I (Sect. 6.5.10, Eq. 6-15) | [8 empty] | I = | 1 | (Table 6-1)
qh = | 18.0597 | psf | qh = 0.00256*Kh*Kzt*Kd*V^2*I (qz evaluated at z = h) | [5 empty] | qh = | 18.0597
Design Net External Wind Pressures (Sect. 6.5.12.2.2):
p = qh*[(GCpf) - (+/-GCpi)] (psf, Eq. 6-18)
Wall and Roof End Zone Widths 'a' and '2*a' (Fig. 6-10):
a = | 14.666 | ft.
2*a = | 29.332 | ft.
MWFRS Wind Load for Transverse Direction |  |  |  | MWFRS Wind Load for Longitudinal Direction
Surface | GCpf | p = Net Pressures (psf) |  | Surface | *GCpf | p = Net Pressures (psf)
|  | (w/ +GCpi) | (w/ -GCpi) |  |  | (w/ +GCpi) | (w/ -GCpi)
Zone 1 | 0.51642 | 6.0757 | 12.5772 | Zone 1 | 0.4 | 3.9731 | 10.4746
Zone 2 | -0.69 | -15.7119 | -9.2104 | Zone 2 | -0.69 | -15.7119 | -9.2104
Zone 3 | -0.46851 | -11.7119 | -5.2104 | Zone 3 | -0.37 | -9.9328 | -3.4313
Zone 4 | -0.41538 | -10.7523 | -4.2508 | Zone 4 | -0.29 | -8.4881 | -1.9866
Zone 5 | -0.45 | -11.3776 | -4.8761 | Zone 5 | -0.45 | -11.3776 | -4.8761
Zone 6 | -0.45 | -11.3776 | -4.8761 | Zone 6 | -0.45 | -11.3776 | -4.8761
Zone 1E | 0.78015 | 10.8386 | 17.3401 | Zone 1E | 0.61 | 7.7657 | 14.2672
Zone 2E | -1.07 | -22.5746 | -16.0731 | Zone 2E | -1.07 | -22.5746 | -16.0731
Zone 3E | -0.67329 | -15.4101 | -8.9086 | Zone 3E | -0.53 | -12.8224 | -6.3209
Zone 4E | -0.61807 | -14.4128 | -7.9113 | Zone 4E | -0.43 | -11.0164 | -4.5149
*Note: Use roof angle q = 0 degrees for Longitudinal Direction.
For Trans. when GCpf is neg. in Zones 2/2E: |  |  |  | For Long. when GCpf is neg. in Zones 2/2E:
Zones 2/2E dist. = | 50 | ft. |  |  | Zones 2/2E dist. = | 50 | ft.
Remainder of roof Zones 2/2E extending to ridge line shall use roof Zones 3/3E pressure coefficients.
MWFRS Wind Load for Transverse, Torsional Case |  |  |  | MWFRS Wind Load for Long., Torsional Case
Surface | GCpf | p = Net Pressure (psf) |  | Surface | GCpf | p = Net Pressure (psf)
|  | (w/ +GCpi) | (w/ -GCpi) |  |  | (w/ +GCpi) | (w/ -GCpi)
Zone 1T | --- | 1.5189 | 3.1443 | Zone 1T | --- | 0.99328 | 2.6187
Zone 2T | --- | -3.928 | -2.3026 | Zone 2T | --- | -3.928 | -2.3026
Zone 3T | --- | -2.928 | -1.3026 | Zone 3T | --- | -2.4832 | -0.85784
Zone 4T | --- | -2.6881 | -1.0627 | Zone 4T | --- | -2.122 | -0.49664
Notes: 1. For Transverse, Longitudinal, and Torsional Cases:
Zone 1 is windward wall for interior zone. |  |  |  | Zone 1E is windward wall for end zone.
Zone 2 is windward roof for interior zone. |  |  |  | Zone 2E is windward roof for end zone.
Zone 3 is leeward roof for interior zone. |  |  |  | Zone 3E is leeward roof for end zone.
Zone 4 is leeward wall for interior zone. |  |  |  | Zone 4E is leeward wall for end zone.
Zones 5 and 6 are sidewalls.
Zone 1T is windward wall for torsional case |  |  |  | Zone 2T is windward roof for torsional case.
Zone 3T is leeward roof for torsional case |  |  |  | Zone 4T is leeward wall for torsional case.
2. (+) and (-) signs signify wind pressures acting toward & away from respective surfaces.
3. Building must be designed for all wind directions using the 8 load cases shown below. The
load cases are applied to each building corner in turn as the reference corner.
4. Wind loads for torsional cases are 25% of respective transverse or longitudinal zone load values.
Torsional loading shall apply to all 8 basic load cases applied at each reference corner.
Exception: One-story buildings with "h" <= 30', buildings <= 2 stories framed with light frame
construction, and buildings <=2 stories designed with flexible diaphragms need not be
designed for torsional load cases.
5. Per Code Section 6.1.4.1, the minimum wind load for MWFRS shall not be less than 10 psf.
6. References | : a. ASCE 7-05, "Minimum Design Loads for Buildings and Other Structures".
b. "Guide to the Use of the Wind Load Provisions of ASCE 7-05"
by: Kishor C. Mehta and William L. Coulbourne (2010).
Low-Rise
Buildings
h <= 60'
Note on B9: The Basic Design Wind Speed, V (mph), corresponds to a 3-second gust speed at 33' above ground in Exposure Category "C" and is associated with an annual probability of 0.02 of being equaled or exceeded (50-year mean recurrence interval). For Basic Wind Speed Map (Fig. 6-1) see 'Wind Map' worksheet of this workbook.
Note on B10: TABLE 1-1 Occupancy Category of Buildings and Other Structures for Flood, Wind, Snow, Earthquake, and Ice Loads Nature of Occupancy Occupancy Category Buildings and structures that represent a low hazard to human life in the event of failure including, I but not limited to: - Agriculture facilities - Certain temporary facilities - Minor storage facilities Buildings and other structures except those listed in Categories I, III and IV II Buildings and other structures that represent a substantial hazard to human life in the event of III failure including, but not limited to: - Buildings and other structures where more than 300 people congregate in one area - Buildings and other structures with day-care facilities with capacity greater than 150 - Elementary or secondary school facilities with capacity greater than 250 - Colleges & adult education facilities with a capacity greater than 500 - Health care facilities with a capacity greater than 50 resident patients but not having surgery or emergency treatment facilities - Jails and detention facilities Buildings and other structures, not includes in Occupancy Category IV, with potential to cause substantial economic impact and/or mass disruption of day-to-day civilian life in event of failure, including, but not limited to: - Power generating stations, water treatment facilities, sewage treatment facilities, and telecommunication centers - Buildings and structures not included in Category IV containing sufficient quantities of toxic, explosive, or other hazardous materials dangerous to the public if released Buildings and other structures designated as essential facilities including, but not limited to: IV - Hospitals and health care facilities having surgery or emergency treatment facilities - Fire, rescue and police stations and emergency vehicle garages - Designated earthquake, hurricane or other emergency shelters - Designated emergency preparedness, communication, and operation centers and other facilities required for emergency response - Power-generating stations and other public utility facilities required in an emergency - Ancillary structures required for operation of Category IV structures during an emergency - Aviation control towers, air traffic control centers and emergency aircraft hangars - Water storage facilities and pump structures required to maintain water pressure for fire suppression - Buildings and other structures having critical national defense functions - Buildings and structures containing extremely hazardous materials where quantity of material exceeds a threshold quantity established by authority having jurisdiction
Note on B11: Surface Roughness Categories for the purpose of assigning Exposure Category are defined as follows: Surface Roughness "B": Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single family dwellings or larger. Surface Roughness "C": Open terrain with scattered obstructions having heights generally < 30 ft. This category includes flat open country, grass lands, and all water surfaces in hurricane prone regions. Surface Roughness "D": Flat, unobstructed areas and water surfaces outside hurricane prone regions. This category includes smooth mud flats, salt flats, and unbroken ice. Exposure Categories are defined as follows: Exposure "B": Exposure B shall apply where the ground surface roughness condition, as defined by Surface Roughness B, prevails in the upwind direction for a distance of at least 2600 ft. or 20 times the building height, whichever is greater. Exception: For buildings whose mean roof height <= 30 ft., the upwind distance may be reduced to 1500 ft. Exposure "C": Exposure C shall apply for all cases where exposures B and D do not apply. Exposure "D": Exposure D shall apply where the ground surface roughness, as defined by Surface Roughness D, prevails in the upwind direction for a distance >= 5,000 ft. or 20 times the building height, whichever is greater. Exposure D shall extend into downwind areas of Surface Roughness B or C for a distance of 600 ft. or 20 times the height of the building, whichever is greater.
Note on B13: The eave height, 'he', is the distance from the ground surface adjacent to the building to the roof eave line at a particular wall. If the height of the eave varies along the wall, the average height shall be used.
Note on B16: This program assumes that a Gable roof is symmetrical, as the ridge line is assumed in the center of the building width. For flat roofs (roof angle = 0 degrees), either Gable or Monoslope may be used.
Note on B17: The Topographic Factor, Kzt, accounts for effect of wind speed-up over isolated hills and escarpments (Sect. 6.5.7 and Fig. 6-4). Kzt = (1+K1*K2*K3)^2 (Eq. 6-3), where: H = height of hill or escarpment relative to the upwind terrain, in feet. Lh = Distance upwind of crest to where the difference in ground elevation is half the height of hill or escarpment, in feet. K1 = factor to account for shape of topographic feature and maximum speed-up effect. K2 = factor to account for reduction in speed-up with distance upwind or downwind of crest. K3 = factor to account for reduction in speed-up with height above local terrain. x = distance (upwind or downwind) from the crest to the building site, in feet. z = height above local ground level, in feet. The effect of wind speed-up shall not be required to be considered (Kzt = 1.0) when H/Lh < 0.2, or H < 15' for Exposures 'C' and 'D', or H < 60' for Exposure 'B'.
Note on B18: Wind Directionality Factor, Kd (Table 6-4) Structure Type Kd Buildings Main Wind-Force Resisting System 0.85 Components and Cladding 0.85 Note: this factor shall only be applied when used in conjunction with load combinations specified in Sect. 2.3 and 2.4. Otherwise, use Kd = 1.0.
Note on B19: This worksheet assumes either Enclosed or Partially Enclosed buildings, and does not consider open buildings. 1. An enclosed building is a building that does not comply with the requirements for open or partially enclosed buildings. 2. An open building is a structure having all walls at least 80% open. 3. A partially enclosed building complies with both of the following conditions: a. the total area of openings in a wall that receives positive external pressure exceeds the sum of the areas of the openings in the balance of the building envelope (walls and roof) by more than 10%; and b. the total area of openings in a wall that receives positive external pressure exceeds 4 sq ft or 1% of the area of that wall, whichever is smaller, and the % of openings in balance of the building envelope does not exceed 20%.
Note on B25: The building Mean Roof Height, h, is determined as follows: For buildings with roof angle > 10 degrees: h = (hr+he)/2 For buildings with roof angle <= 10 degrees: h = he
Note on C27: For an enclosed or partially enclosed building to be classified as a Low-Rise building, the following 2 conditions must both be met: 1. The building mean roof height, h, must be <= 60 ft. 2. The building mean roof height, h, does not exceed the least horizontal dimension, L or B.
Note on C30: External Pressure Coefficients, GCpf, for MWFRS ( Fig. 6-10): Roof Angle,q Building Surface (Zone) (deg.) 1 2 3 4 5 6 1E 2E 3E 4E 0-5 0.40 -0.69 -0.37 -0.29 -0.45 -0.45 0.61 -1.07 -0.53 -0.43 20 0.53 -0.69 -0.48 -0.43 -0.45 -0.45 0.80 -1.07 -0.69 -0.64 30-45 0.56 0.21 -0.43 -0.37 -0.45 -0.45 0.69 0.27 -0.53 -0.48 90 0.56 0.56 -0.37 -0.37 -0.45 -0.45 0.69 0.69 -0.48 -0.48
Note on C38: Terrain Exposure Constants (Table 6-2) Exposure Category a zg (ft) B 7.0 1,200 C 9.5 900 D 11.5 700
Note on C41: Importance Factor, I (Table 6-1): Non-Hurricane Prone Regions Hurricane Prone Regions Category and Hurricane Prone Regions with V > 100 mph with V = 85-100 mph and Alaska I 0.87 0.77 II 1.00 1.00 III 1.15 1.15 IV 1.15 1.15 Note: in the U.S. and its territories hurricane prone regions are defined as: 1. U.S. Atlantic Ocean and Gulf of Mexico coasts where the basic wind speed is > 90 mph. 2. Hawaii, Puerto Rico, Guam, Virgin Islands, and American Samoa.
Note on C68: For Transverse Load Case the roof pressure coefficient, GCpf, when negative in Zone 2 or 2E, shall be applied in Zone 2/2E for a distance from the edge of the roof equal to 0.5 times the horizontal dimension of the building parallel to the direction of the MWFRS being designed or 2.5*he at the windward wall, whichever is less; the remainder of Zone 2/2E extending to the ridge line shall use the pressure coefficient GCpf for Zone 3/3E.
Note on D45: Per Code Section 6.1.4.1, the minimum wind load to be used in the design of the Main Wind-Force Resisting System shall not be less than 10 psf.
Note on D48: Width 'a' is equal to 10% of least horizontal dimension or 0.4*h, whichever is smaller, but not less than either 4% of least horizontal dimension or 3'.
Note on D54: Per Code Section 6.1.4.1, the minimum wind load to be used in the design of the MWFRS shall not be less than 10 psf multiplied by the area of the building or structure projected onto a vertical plane normal to the assumed wind direction.
Note on D73: Per Code Section 6.1.4.1, the minimum wind load to be used in the design of the MWFRS shall not be less than 10 psf multiplied by the area of the building or structure projected onto a vertical plane normal to the assumed wind direction.
Note on E32: Internal Pressure Coefficients, GCpi (Figure 6-5) Condition (+/-) GCpi Partially enclosed buildings +0.55, -0.55 Enclosed buildings +0.18, -0.18 Per Sect. 6.5.11.1, for a partially enclosed building containing a single, unpartitioned large volume, the GCpi coefficients shall be multiplied by the following reduction factor, Ri: Ri = 1.0 or Ri = 0.5*(1+(1/(1+Vi/(22800*Aog))^0.5)) <= 1.0 where: Aog = total area of openings in the building envelope (walls and roof, ft.^2). Vi = unpartitioned internal volume (ft.^3). Note: This program assumes NO reduction of the GCpi coefficients for large volume buildings. Thus, Ri = 1.0.
Note on H3: For an enclosed or partially enclosed building to be classified as a Low-Rise building, the following 2 conditions must both be met: 1. The building mean roof height, h, must be <= 60 ft. 2. The building mean roof height, h, does not exceed the least horizontal dimension, L or B.
Note on H54: Per Code Section 6.1.4.1, the minimum wind load to be used in the design of the MWFRS shall not be less than 10 psf multiplied by the area of the building or structure projected onto a vertical plane normal to the assumed wind direction.
Note on H68: For Longitudinal Load Case the roof pressure coefficient, GCpf, when negative in Zone 2 or 2E, shall be applied in Zone 2/2E for a distance from the edge of the roof equal to 0.5 times the horizontal dimension of the building parallel to the direction of the MWFRS being designed or 2.5*he at the windward wall, whichever is less; the remainder of Zone 2/2E extending to the ridge line shall use the pressure coefficient GCpf for Zone 3/3E.
Note on H73: Per Code Section 6.1.4.1, the minimum wind load to be used in the design of the MWFRS shall not be less than 10 psf multiplied by the area of the building or structure projected onto a vertical plane normal to the assumed wind direction.
Note on AA1: "ASCE705W.xls" written by: Alex Tomanovich, P.E.
q o
L
B
hr
he
h<=60'
Wind
Plan
Elevation
L

## MWFRS (Any Ht.)
WIND LOADING ANALYSIS - Main Wind-Force Resisting System | [8 empty] | CALCULATIONS: | [6 empty] | Version 1.4
Per ASCE 7-05 Code for Enclosed or Partially Enclosed Buildings
Using Method 2: Analytical Procedure (Section 6.5) for Buildings of Any Height | [6 empty] | Normal |  | For Normal/Parallel to Ridge Wind Direction: |  |  |  | Roof Angle, q = | 0
Job Name: |  |  | Subject: |  |  |  | Parallel |  | L & B or B & L: |  |  |  | Mean Roof Ht., h = | 157
Job Number: |  |  | Originator: |  | Checker: |  | I |  | L = | 100 | ft. |  | Applicable L/B ratio = | 0.5
[7 empty] | II |  | B = | 200 | ft. |  | Applicable h/L ratio = | 1.57
Input Data: | [6 empty] | III
[7 empty] | IV |  | Wall Pressure Coefficients, Cp (Fig. 6-6):
Wind Direction = | Normal | (Normal or Parallel to building ridge) |  |  |  |  | B |  | Windward Wall Cp = | 0.8 |  | Applicable Area = | 15700 | (for Roof Cp = -1.3)
Wind Speed, V = | 120 | mph (Wind Map, Figure 6-1) |  |  |  |  | C |  | Leeward Wall Cp = | -0.5 |  | Reduction Factor = | 0.8 | (for Roof Cp = -1.3)
Bldg. Classification = | II | (Table 1-1 Occupancy Cat.) |  |  |  |  | D |  | Side Walls Cp = | -0.7
Exposure Category = | B | (Sect. 6.5.6) |  |  |  |  | Gable
Ridge Height, hr = | 157 | ft. (hr >= he) |  |  |  |  | Monoslope |  | Roof Pressure Coefficients, Cp (Fig. 6-6):
Eave Height, he = | 157 | ft. (he <= hr) |  |  |  |  | Y |  | Windward Roof Cp Values |  |  | Leeward Roof Cp Values
Building Width = | 100 | ft. (Normal to Building Ridge) |  |  |  |  | N |  | For 10 <= q <= 45: |  |  | For 10 <= q <= 45:
Building Length = | 200 | ft. (Parallel to Building Ridge) | [6 empty] | For h/L<=0.25: | N.A. | N.A. |  | For h/L<=0.25: | N.A.
Roof Type = | Monoslope | (Gable or Monoslope) | [6 empty] | For h/L=0.5: | N.A. | N.A. |  | For h/L=0.5: | N.A.
Topo. Factor, Kzt = | 1 | (Sect. 6.5.7 & Figure 6-4) | [6 empty] | For h/L>=1.0: | N.A. | N.A. |  | For h/L>=1.0: | N.A.
Direct. Factor, Kd = | 0.85 | (Table 6-4) | [6 empty] | actual h/L = | N.A. | N.A. |  | actual h/L = | N.A.
Enclosed? (Y/N) | Y | (Sect. 6.2 & Figure 6-5) | [6 empty] | Use Roof Cp = | N.A. | N.A. |  | Use Roof Cp = | N.A.
Hurricane Region? | N
Damping Ratio, b = | 0.03 | (Suggested Range = 0.010-0.070) | [6 empty] | For q < 10 for Wind Normal to Ridge: |  |  | For All q for Wind Parallel to Ridge:
Period Coef., Ct = | 0.02 | (Suggested Range = 0.020-0.035) | [5 empty] | for 0 to h/2 | Zone #1 Roof Cp = | -1.04 | -0.18 |  | Zone #1 Roof Cp = | N.A. | N.A.
|  | (Assume: T = Ct*h^(3/4) , and f = 1/T) | [5 empty] | for h/2 to h | Zone #2 Roof Cp = | -0.7 | -0.18 |  | Zone #2 Roof Cp = | N.A. | N.A.
[8 empty] | for h to 2*h | Zone #3 Roof Cp = | N.A. | N.A. |  | Zone #3 Roof Cp = | N.A. | N.A.
Resulting Parameters and Coefficients: | [7 empty] | for > 2*h | Zone #4 Roof Cp = | N.A. | N.A. |  | Zone #4 Roof Cp = | N.A. | N.A.
Roof Angle, q = | 0 | deg. | [6 empty] | Positive & Negative Internal Pressure Coefficients, GCpi (Figure 6-5):
Mean Roof Ht., h = | 157 | ft. (h = he, for roof angle <=10 deg.) |  |  |  | L = 100 ft. |  |  | +GCpi Coef. (PIP) = | 0.18
Windward Wall Cp = | 0.8 | (Fig. 6-6) |  |  |  | B = 200 ft. |  |  | -GCpi Coef. (NIP) = | -0.18
Leeward Wall Cp = | -0.5 | (Fig. 6-6)
Side Walls Cp = | -0.7 | (Fig. 6-6) | [6 empty] | Determine a, zg, Kh, I, and qh:
Roof Cp (zone #1) = | -1.04 | -0.18 | (Fig. 6-6) | (zone #1 for 0 to h/2) |  |  |  |  | a = | 7 | (Table 6-2)
Roof Cp (zone #2) = | -0.7 | -0.18 | (Fig. 6-6) | (zone #2 for h/2 to h) |  |  |  |  | zg = | 1200 | (Table 6-2)
Roof Cp (zone #3) = | N.A. | N.A. | (Fig. 6-6) | (zone #3 for h to 2*h) |  |  |  |  | Kh = | 1.1242 | (Table 6-3, Case 2a)
Roof Cp (zone #4) = | N.A. | N.A. | (Fig. 6-6) | (zone #4 for > 2*h) |  |  |  |  | I = | 1 | (Table 6-1)
+GCpi Coef. = | 0.18 | (Figure 6-5) | (positive internal pressure) | [5 empty] | qh = | 35.225
-GCpi Coef. = | -0.18 | (Figure 6-5) | (negative internal pressure)
If z <= 15 then: Kz = 2.01*(15/zg)^(2/a) , If z > 15 then: Kz = 2.01*(z/zg)^(2/a) (Table 6-3, Case 2a)
a = | 7 | zg = | 1200 | (Table 6-2)
Kh = | 1.1242 | (Kh = Kz evaluated at z = h)
I = | 1 | (Table 6-1) | (Importance factor)
Velocity Pressure: qz = 0.00256*Kz*Kzt*Kd*V^2*I (Sect. 6.5.10, Eq. 6-15)
qh = | 35.225 | psf | qh = 0.00256*Kh*Kzt*Kd*V^2*I (qz evaluated at z = h)
Ratio h/L = | 1.57 | freq., f = | 1.1273 | hz. | (f >= 1, Rigid structure)
Gust Factor, G = | 0.8183 | (Sect. 6.5.8)
Design Net External Wind Pressures (Sect. 6.5.12.2):
p = qz*G*Cp - qi*(+/-GCpi) for windward wall (psf), where: qi =qh (Eq. 6-17, Sect. 6.5.12.2.1)
p = qh*G*Cp - qi*(+/-GCpi) for leeward wall, sidewalls, and roof (psf), where: qi = qh (Sect. 6.5.12.2.1)
Normal to Ridge Wind Load Tabulation for MWFRS - Buildings of Any Height
Surface | z | Kz | qz | Cp | p = Net Design Press. (psf) | [11 empty] | User Input for Height, z (ft.):
| (ft.) |  | (psf) |  | (w/ +GCpi) | (w/ -GCpi) | [10 empty] | N | Use Input Values?
Windward Wall | 0 | 0.57472 | 18.0085 | 0.8 | 5.4486 | 18.1297
| 15 | 0.57472 | 18.0085 | 0.8 | 5.4486 | 18.1297
| 20 | 0.62395 | 19.5512 | 0.8 | 6.4586 | 19.1396
| 25 | 0.66503 | 20.8383 | 0.8 | 7.3012 | 19.9822
| 30 | 0.70059 | 21.9526 | 0.8 | 8.0306 | 20.7116
| 35 | 0.73214 | 22.9411 | 0.8 | 8.6777 | 21.3587
| 40 | 0.76061 | 23.8332 | 0.8 | 9.2618 | 21.9428
| 45 | 0.78664 | 24.6489 | 0.8 | 9.7958 | 22.4768
| 50 | 0.81068 | 25.4022 | 0.8 | 10.2889 | 22.9699
| 55 | 0.83306 | 26.1034 | 0.8 | 10.748 | 23.429
| 60 | 0.85403 | 26.7605 | 0.8 | 11.1781 | 23.8591
| 70 | 0.89248 | 27.9655 | 0.8 | 11.9669 | 24.6479
| 80 | 0.92719 | 29.053 | 0.8 | 12.6789 | 25.3599
| 90 | 0.95893 | 30.0474 | 0.8 | 13.3298 | 26.0108
| 100 | 0.98823 | 30.9656 | 0.8 | 13.9309 | 26.612
| 120 | 1.0411 | 32.6214 | 0.8 | 15.0149 | 27.6959
| 140 | 1.088 | 34.0903 | 0.8 | 15.9765 | 28.6575
For z = hr: | 157 | 1.1242 | 35.225 | 0.8 | 16.7193 | 29.4003
For z = he: | 157 | 1.1242 | 35.225 | 0.8 | 16.7193 | 29.4003
For z = h: | 157 | 1.1242 | 35.225 | 0.8 | 16.7193 | 29.4003
Leeward Wall | All | - | - | -0.5 | -20.7529 | -8.0719
Side Walls | All | - | - | -0.7 | -26.5179 | -13.8369
Roof (zone #1) cond. 1 | - | - | - | -1.04 | -36.3183 | -23.6373
Roof (zone #1) cond. 2 | - | - | - | -0.18 | -11.529 | 1.152
Roof (zone #2) cond. 1 | - | - | - | -0.7 | -26.5179 | -13.8369
Roof (zone #2) cond. 2 | - | - | - | -0.18 | -11.529 | 1.152
Notes: 1. (+) and (-) signs signify wind pressures acting toward & away from respective surfaces.
2. Per Code Section 6.1.4.1, the minimum wind load for MWFRS shall not be less than 10 psf.
3. References | : a. ASCE 7-05, "Minimum Design Loads for Buildings and Other Structures".
b. "Guide to the Use of the Wind Load Provisions of ASCE 7-05"
by: Kishor C. Mehta and William L. Coulbourne (2010).
4. Roof zone #1 is applied for horizontal distance of 0 to h/2 from windward edge.
5. Roof zone #2 is applied for horizontal distance of h/2 to h from windward edge.
Determination of Gust Effect Factor, G:
Is Building Flexible? | No | f >=1 Hz.
1: Simplified Method for Rigid Building
G = | 0.85
Parameters Used in Both Item #2 and Item #3 Calculations (from Table 6-2):
a^ = | 0.14286
b^ = | 0.84
a(bar) = | 0.25
b(bar) = | 0.45
c = | 0.3
l = | 320 | ft.
e(bar) = | 0.33333
z(min) = | 30 | ft.
Calculated Parameters Used in Both Rigid and/or Flexible Building Calculations:
z(bar) = | 94.2 | = 0.6*h , but not < z(min) , ft.
Iz(bar) = | 0.25188 | = c*(33/z(bar))^(1/6) , Eq. 6-5
Lz(bar) = | 453.9371 | = l*(z(bar)/33)^(e(bar)) , Eq. 6-7
gq = | 3.4 | (3.4, per Sect. 6.5.8.1)
gv = | 3.4 | (3.4, per Sect. 6.5.8.1)
gr = | 4.2179 | = (2*(LN(3600*f)))^(1/2)+0.577/(2*LN(3600*f))^(1/2) , Eq. 6-9
Q = | 0.80543 | = (1/(1+0.63*((B+h)/Lz(bar))^0.63))^(1/2) , Eq. 6-6
2: Calculation of G for Rigid Building
G = | 0.8183 | = 0.925*((1+1.7*gq*Iz(bar)*Q)/(1+1.7*gv*Iz(bar))) , Eq. 6-4
3: Calculation of Gf for Flexible Building
b = | 0.03 | Damping Ratio
Ct = | 0.02 | Period Coefficient
T = | 0.88706 | = Ct*h^(3/4) , sec. (Approximate fundamental period)
f = | 1.1273 | = 1/T , Hz. (Natural Frequency)
V(fps) = | N.A. | = V(mph)*(88/60) , ft./sec.
V(bar,zbar) = | N.A. | = b(bar)*(z(bar)/33)^(a(bar))*V*(88/60) , ft./sec. , Eq. 6-14
N1 = | N.A. | = f*Lz(bar)/(V(bar,zbar)) , Eq. 6-12
Rn = | N.A. | = 7.47*N1/(1+10.3*N1)^(5/3) , Eq. 6-11
hh = | N.A. | = 4.6*f*h/(V(bar,zbar))
Rh = | N.A. | = (1/hh)-1/(2*hh^2)*(1-e^(-2*hh)) for hh>0, or = 1 for hh=0 ,Eq. 6-13a,b
hb = | N.A. | = 4.6*f*B/(V(bar,zbar))
RB = | N.A. | = (1/hb)-1/(2*hb^2)*(1-e^(-2*hb)) for hb>0, or = 1 for hb=0,Eq. 6-13a,b
hd = | N.A. | = 15.4*f*L/(V(bar,zbar))
RL = | N.A. | = (1/hd)-1/(2*hd^2)*(1-e^(-2*hd)) for hd>0, or = 1 for hd=0 ,Eq. 6-13a,b
R = | N.A. | = ((1/b)*Rn*Rh*RB*(0.53+0.47*RL))^(1/2) , Eq. 6-10
Gf = | N.A. | = 0.925*(1+1.7*Iz(bar)*(gq^2*Q^2+gr^2*R^2)^(1/2))/(1+1.7*gv*Iz(bar)) ,
Use: G = | 0.8183 |  |  |  |  | Eq. 6-8
Figure 6-9 - Design Wind Load Cases of MWFRS for Buildings of All Heights
Case 1: Full design wind pressure acting on the projected area perpendicular to each principal axis of
the structure, considered separately along each principal axis.
Case 2: Three quarters of the design wind pressure acting on the projected area perpendicular to each
principal axis of the structure in conjunction with a torsional moment as shown, considered
separately for each principal axis.
Case 3: Wind pressure as defined in Case 1, but considered to act simultaneously at 75% of the
specified value. (Note: Load Case 3 would approximate "oblique" applied wind loading.)
Case 4: Wind pressure as defined in Case 2, but considered to act simultaneously at 75% of the
specified value.
Notes: 1. Design wind pressures for windward (Pw) and leeward (PL) faces shall be determined in
accordance with the provisions of Section 6.5.12.2.1 and 6.5.12.2.3 as applicable for buildings
of all heights.
2. Above diagrams show plan views of building.
3. Notation:
Pwx, Pwy = Windward face pressure acting in the X, Y principal axis, respectively.
PLx, PLy = Leeward face pressure acting in the X, Y principal axis, respectively.
e (ex, ey) = Eccentricity for the X, Y principal axis of the structure, respectively.
MT = Torsional moment per unit height acting about a vertical axis of the building.
Note on B9: Actual values of B and L depend on the Wind Direction, and are defined as follows: B = horizontal dimension of building measured normal to wind direction. L = horizontal dimension of building measured parallel to wind direction. Note: Plan view at right depicts case where Wind Direction is Normal to building ridge.
Note on B10: The Basic Design Wind Speed, V (mph), corresponds to a 3-second gust speed at 33' above ground in Exposure Category "C" and is associated with an annual probability of 0.02 of being equaled or exceeded (50-year mean recurrence interval). For Basic Wind Speed Map (Fig. 6-1) see 'Wind Map' worksheet of this workbook.
Note on B11: TABLE 1-1 Occupancy Category of Buildings and Other Structures for Flood, Wind, Snow, Earthquake, and Ice Loads Nature of Occupancy Occupancy Category Buildings and structures that represent a low hazard to human life in the event of failure including, I but not limited to: - Agriculture facilities - Certain temporary facilities - Minor storage facilities Buildings and other structures except those listed in Categories I, III and IV II Buildings and other structures that represent a substantial hazard to human life in the event of III failure including, but not limited to: - Buildings and other structures where more than 300 people congregate in one area - Buildings and other structures with day-care facilities with capacity greater than 150 - Elementary or secondary school facilities with capacity greater than 250 - Colleges & adult education facilities with a capacity greater than 500 - Health care facilities with a capacity greater than 50 resident patients but not having surgery or emergency treatment facilities - Jails and detention facilities Buildings and other structures, not includes in Occupancy Category IV, with potential to cause substantial economic impact and/or mass disruption of day-to-day civilian life in event of failure, including, but not limited to: - Power generating stations, water treatment facilities, sewage treatment facilities, and telecommunication centers - Buildings and structures not included in Category IV containing sufficient quantities of toxic, explosive, or other hazardous materials dangerous to the public if released Buildings and other structures designated as essential facilities including, but not limited to: IV - Hospitals and health care facilities having surgery or emergency treatment facilities - Fire, rescue and police stations and emergency vehicle garages - Designated earthquake, hurricane or other emergency shelters - Designated emergency preparedness, communication, and operation centers and other facilities required for emergency response - Power-generating stations and other public utility facilities required in an emergency - Ancillary structures required for operation of Category IV structures during an emergency - Aviation control towers, air traffic control centers and emergency aircraft hangars - Water storage facilities and pump structures required to maintain water pressure for fire suppression - Buildings and other structures having critical national defense functions - Buildings and structures containing extremely hazardous materials where quantity of material exceeds a threshold quantity established by authority having jurisdiction
Note on B12: Surface Roughness Categories for the purpose of assigning Exposure Category are defined as follows: Surface Roughness "B": Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single family dwellings or larger. Surface Roughness "C": Open terrain with scattered obstructions having heights generally < 30 ft. This category includes flat open country, grass lands, and all water surfaces in hurricane prone regions. Surface Roughness "D": Flat, unobstructed areas and water surfaces outside hurricane prone regions. This category includes smooth mud flats, salt flats, and unbroken ice. Exposure Categories are defined as follows: Exposure "B": Exposure B shall apply where the ground surface roughness condition, as defined by Surface Roughness B, prevails in the upwind direction for a distance of at least 2600 ft. or 20 times the building height, whichever is greater. Exception: For buildings whose mean roof height <= 30 ft., the upwind distance may be reduced to 1500 ft. Exposure "C": Exposure C shall apply for all cases where exposures B and D do not apply. Exposure "D": Exposure D shall apply where the ground surface roughness, as defined by Surface Roughness D, prevails in the upwind direction for a distance >= 5,000 ft. or 20 times the building height, whichever is greater. Exposure D shall extend into downwind areas of Surface Roughness B or C for a distance of 600 ft. or 20 times the height of the building, whichever is greater.
Note on B14: The eave height, 'he', is the distance from the ground surface adjacent to the building to the roof eave line at a particular wall. If the height of the eave varies along the wall, the average height shall be used.
Note on B17: This program assumes that a Gable roof is symmetrical, as the ridge line is assumed in the center of the building width, L. For flat roofs (roof angle = 0 degrees), either Gable or Monoslope may be used.
Note on B18: The Topographic Factor, Kzt, accounts for effect of wind speed-up over isolated hills and escarpments (Sect. 6.5.7 and Fig. 6-4). Kzt = (1+K1*K2*K3)^2 (Eq. 6-3), where: H = height of hill or escarpment relative to the upwind terrain, in feet. Lh = Distance upwind of crest to where the difference in ground elevation is half the height of hill or escarpment, in feet. K1 = factor to account for shape of topographic feature and maximum speed-up effect. K2 = factor to account for reduction in speed-up with distance upwind or downwind of crest. K3 = factor to account for reduction in speed-up with height above local terrain. x = distance (upwind or downwind) from the crest to the building site, in feet. z = height above local ground level, in feet. The effect of wind speed-up shall not be required to be considered (Kzt = 1.0) when H/Lh < 0.2, or H < 15' for Exposures 'C' and 'D', or H < 60' for Exposure 'B'.
Note on B19: Wind Directionality Factor, Kd (Table 6-4) Structure Type Kd Buildings Main Wind-Force Resisting System 0.85 Components and Cladding 0.85 Note: this factor shall only be applied when used in conjunction with load combinations specified in Sect. 2.3 and 2.4. Otherwise, use Kd = 1.0.
Note on B20: This worksheet assumes either Enclosed or Partially Enclosed buildings, and does not consider open buildings. 1. An enclosed building is a building that does not comply with the requirements for open or partially enclosed buildings. 2. An open building is a structure having all walls at least 80% open. 3. A partially enclosed building complies with both of the following conditions: a. the total area of openings in a wall that receives positive external pressure exceeds the sum of the areas of the openings in the balance of the building envelope (walls and roof) by more than 10%; and b. the total area of openings in a wall that receives positive external pressure exceeds 4 sq ft or 1% of the area of that wall, whichever is smaller, and the % of openings in balance of the building envelope does not exceed 20%.
Note on B22: The Damping Ratio, b, is the percent of critical damping. It is only used in the calculation of the Gust Factor, Gf, when a building is considered "flexible". A building is considered "flexible" when it has a natural frequency, f < 1 hz. Otherwise the building is considered "rigid". Suggested range of values is from 0.010 to 0.070 as indicated below: Material/Construction b (Damping Ratio) Welded steel, 0.01 to 0.02 prestressed concrete Reinforced concrete 0.03 to 0.05 Bolted or riveted steel, 0.05 to 0.07 wood Note: if the building is "flexible", the smaller the value of the damping ratio, the larger the gust effect factor, Gf, becomes.
Note on B23: The building Period Coefficient, Ct, has suggested range of values from 0.020 to 0.035. It is used in the equation for the assumed period of the building: T = Ct*h^3/4. Then the natural frequency, f, is determined by: f = 1/T. It is only used in the calculation of the Gust Factor, Gf, when a building is considered "flexible". A building is considered "flexible" when it has a natural frequency, f < 1 hz. Otherwise the building is considered "rigid". Note: if the period, T, or the natural frequency, f, is already known (obtained by other means), then the value of Ct may be "manipulated" to give the desired results for T and f.
Note on B29: The building Mean Roof Height, h, is determined as follows: For buildings with roof angle > 10 degrees: h = (hr+he)/2 For buildings with roof angle <= 10 degrees: h = he
Note on B47: If the structure is "rigid", then the minimum of either the calculated value of 'G' for "rigid" structures or 0.85 is used. If the structure is "flexible" then the calculated value of 'G' is used. (See calculations on page 3.)
Note on B108: Buildings which have a natural frequency, f >= 1 Hz are considered "rigid". Buildings which have a natural frequency, f < 1 Hz are considered "flexible".
Note on B124: The Equivalent Height of the Building, z(bar). z(bar) = 0.6*h but not less than z(min) from Table 6-2. where: h = building mean roof height
Note on B125: The Intensity of Turbulence at height = z(bar). Iz(bar) = c*(33/z(bar))^(1/6)
Note on B126: The Integral Length Scale of Turbulence at the equivalent height. Lz(bar) = l*(z(bar)/33)^(e (bar))
Note on B127: Peak Factor for background response: gq = 3.4 (per Sect. 6.5.8.1)
Note on B128: Peak Factor for wind response: gv = 3.4 (per Sect. 6.5.8.1)
Note on B129: Peak Factor for resonant response: gr = (2*(LN(3600*f)))^(1/2)+0.577/(2*LN(3600*f))^(1/2) Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B130: The Background Response Factor, Q. Q = (1/(1+0.63*((B+h)/Lz(bar))^0.63))^(1/2) where: B = building width normal to wind h = building mean roof height
Note on B133: The Gust Effect Factor, G, for a "rigid" structure. G = 0.925*((1+1.7*gq*Iz(bar)*Q)/(1+1.7*gv*Iz(bar))) where: gq = 3.4 and gv = 3.4
Note on B140: The Basic Wind Speed, V, converted from units of mph to ft/sec. V(fps) = V(mph)*(88/60)
Note on B141: The Mean Hourly Wind Speed, V(bar,zbar). V(bar,zbar) = b(bar)*(z(bar)/33)^(a(bar))*V*(88/60)
Note on B142: N1 = f*Lz(bar)/(V(bar,zbar)) Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B143: Rn = 7.47*N1/(1+10.3*N1)^(5/3)
Note on B144: hh = 4.6*f*h/(V(bar,zbar)) Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B145: Rh = (1/hh)-1/(2*hh^2)*(1-e^(-2*hh)) for hh > 0 or: Rh = 1 for hh = 0
Note on B146: hB =4.6*f*B/(V(bar,zbar)) where: B = building width normal to wind Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B147: RB = (1/hB)-1/(2*hB^2)*(1-e^(-2*hB)) for hB > 0 or: RB = 1 for hB = 0
Note on B148: hL = 15.4*f*L/(V(bar,zbar)) where: L = depth of building parallel to wind Note: the symbol, f, was subsituted for the original symbol, n1, in the equation above.
Note on B149: RL = (1/hL)-1/(2*hL^2)*(1-e^(-2*hL)) for hL > 0 or: RL = 1 for hL = 0
Note on B150: The Resonant Response Factor, R. R = ((1/b)*Rn*Rh*Rb*(0.53+0.47*Rd))^1/2
Note on B151: The Gust Effect Factor, Gf, for a "flexible" building. Gf = 0.925*(1+1.7*Iz(bar)*(gq^2*Q^2+gr^2*R^2)^(1/2))/(1+1.7*gv*Iz(bar))
Note on B152: For a rigid building, the smaller of the value of either 0.85 or the value as calculated in item #2 is used for the gust effect factor, G.
Note on C30: Wall External Pressure Coefficients, Cp (Fig. 6-6) Surface L/B Cp Use With Windward All values 0.8 qz Wall Leeward 0-1 -0.5 Wall 2 -0.3 qh >=4 -0.2 Side Walls All values -0.7 qh
Note on C37: Internal Pressure Coefficients, GCpi (Figure 6-5) Condition (+/-) GCpi Partially enclosed buildings +0.55, -0.55 Enclosed buildings +0.18, -0.18 Per Sect. 6.5.11.1, for a partially enclosed building containing a single, unpartitioned large volume, the GCpi coefficients shall be multiplied by the following reduction factor, Ri: Ri = 1.0 or Ri = 0.5*(1+(1/(1+Vi/(22800*Aog))^0.5)) <= 1.0 where: Aog = total area of openings in the building envelope (walls and roof, ft.^2). Vi = unpartitioned internal volume (ft.^3). Note: This program assumes NO reduction of the GCpi coefficients for large volume buildings. Thus, Ri = 1.0.
Note on C43: Importance Factor, I (Table 6-1): Non-Hurricane Prone Regions Hurricane Prone Regions Category and Hurricane Prone Regions with V > 100 mph with V = 85-100 mph and Alaska I 0.87 0.77 II 1.00 1.00 III 1.15 1.15 IV 1.15 1.15 Note: in the U.S. and its territories hurricane prone regions are defined as: 1. U.S. Atlantic Ocean and Gulf of Mexico coasts where the basic wind speed is > 90 mph. 2. Hawaii, Puerto Rico, Guam, Virgin Islands, and American Samoa.
Note on C110: The Gust Effect Factor, G, for rigid buildings may be simply taken as 0.85 for all building exposure conditions.
Note on C132: The Gust Effect Factor, G, for a rigid building as calculated from Eqn. 6-4.
Note on C135: The Gust Effect Factor, Gf, for a flexible building as calculated from Eqn 6-8. Note: calculations below are applicable only for "flexible" buildings which have a natural frequency, f < 1 hz.
Note on D33: Roof External Pressure Coefficients, Cp, for Use with qh (Fig. 6-6): Windward Leeward Wind Angle, q (degrees) Angle, q (degrees) Direction h/L 10 15 20 25 30 35 45 10 15 >=20 <=0.25 -0.7 -0.5 -0.3 -0.2 -0.2 0.0* 0.0* -0.3 -0.5 -0.6 Normal to -0.18 0.0* 0.2 0.3 0.3 0.4 0.4 ridge for 0.5 -0.9 -0.7 -0.4 -0.3 -0.2 -0.2 0.0* -0.5 -0.5 -0.6 q>=10 -0.18 -0.18 0.0* 0.2 0.2 0.3 0.4 >=1.0 -1.3** -1.0 -0.7 -0.5 -0.3 -0.2 0.0* -0.7 -0.6 -0.6 -0.18 -0.18 -0.18 0.0* 0.2 0.2 0.3 Horiz. dist. from Normal to windward edge Cp *Value is provided for interpolation purposes. ridge for 0 to h/2 -0.9,-0.18 **Value can be reduced linearly with area over which q<10 & <=0.5 h/2 to h -0.9,-0.18 it is applicable as follows: Area Reduction Parallel to h to 2*h -0.5,-0.18 (sq ft) Factor ridge for >2*h -0.3,-0.18 <=100 1.0 all q >=1.0 0 to h/2 -1.3**,-0.18 250* 0.9 >h/2 -0.7,-0.18 >=1000 0.8 * Note: The change in value shown above from 200 to the 250 shown reflects the errata that was issued on 6/28/07 for the same situation in the ASCE 7-02 Code.
Note on D48: Per Code Section 6.1.4.1, the minimum wind load to be used in the design of the Main Wind-Force Resisting System shall not be less than 10 psf.
Note on E41: Terrain Exposure Constants (Table 6-2) Exposure Category a zg (ft) B 7.0 1,200 C 9.5 900 D 11.5 700
Note on E113: Terrain Exposure Constants (Table 6-2) Exposure a zg(ft) a^ b^ a(bar) b(bar) c l(ft) e z(min) B 7.0 1200 1/7 0.84 1/4.0 0.45 0.30 320 1/3.0 30 C 9.5 900 1/9.5 1.00 1/6.5 0.65 0.20 500 1/5.0 15 D 11.5 700 1/11.5 1.07 1/9.0 0.80 0.15 650 1/8.0 7 Note: z(min) = minimum height used to ensure that the equivalent height z(bar) is greater of 0.6*h or z(min). For buildings with h<= z(min), z(bar) shall be taken as z(min).
Note on G3: Note: This program assumes buildings are a maximum of 500 feet tall.
Note on G29: Note: 'L' is the horizontal dimension of the building measured parallel to the wind direction.
Note on G30: Note: 'B' is the horizontal dimension of the building measured normal to the wind direction.
Note on G54: Per Code Section 6.1.4.1, the minimum wind load to be used in the design of the MWFRS shall not be less than 10 psf multiplied by the area of the building or structure projected onto a vertical plane normal to the assumed wind direction.
Note on AA1: "ASCE705W.xls" written by: Alex Tomanovich, P.E.
q o
L
B
hr
he
h
Plan
Elevation
L
Wind

## MWFRS (Case 2)
WIND LOADING ANALYSIS - Main Wind-Force Resisting System | [8 empty] | Version 1.4
Per ASCE 7-05 Code Method 2 for Enclosed or Partially Enclosed Buildings
Design Wind Load Case 2 from Figure 6-9
Job Name: |  |  |  | Subject:
Job Number: |  |  |  | Originator: |  |  | Checker:
ASCE 7-05 Figure 6-9 - Design Wind Load Case 2
P2
For Case 2 (x-direction wind)
P1
MT
P1
P2
Application of Additional Torsional Moment
Input Data: |  |  |  | Results:
| Bldg. Dimension (x-dir.) = | 100 | ft. | Length, Bx = | 200 | ft.
| Bldg. Dimension (y-dir.) = | 200 | ft. | Length, By = | 100 | ft.
| Windward, Pwx = | 0.029 | ksf | Eccentricity, ex = | 30 | ft., ex = 0.15*Bx
| Leeward, PLx = | 0.008 | ksf | Tors. Moment, MT = | 166.5 | ft-k, MT=0.75*(Pwx+PLx)*Bx*ex
|  |  |  | Perimeter Force, qw = | 0.0041625 | kips/ft./ft. Ht., qw = MT/(2*Bx*By)
|  |  |  | Applied Load, P1 = | 0.41625 | kips/ft. Ht., P1 = qw*By
|  |  |  | Applied Load, P2 = | 0.8325 | kips/ft. Ht., P2 = qw*Bx
Note: Loadings P1 and P2 are to be applied per ft. of building height.
For Case 2 (y-direction wind)
P2
P1
MT
P1
P2
Application of Additional Torsional Moment
Results:
Input Data: |  |  |  | Length, Bx = | 200 | ft.
| Bldg. Dimension (x-dir.) = | 100 | ft. | Length, By = | 100 | ft.
| Bldg. Dimension (y-dir.) = | 200 | ft. | Eccentricity, ey = | 15 | ft., ey = 0.15*By
| Windward, Pwy = | 0.0298 | ksf | Tors. Moment, MT = | 36.3375 | ft-k, MT=0.75*(Pwy+PLy)*By*ey
| Leeward, PLy = | 0.0025 | ksf | Perimeter Force, qw = | 0.00090844 | kips/ft./ft. Ht., qw = MT/(2*Bx*By)
|  |  |  | Applied Load, P1 = | 0.090844 | kips/ft. Ht., P1 = qw*By
|  |  |  | Applied Load, P2 = | 0.18169 | kips/ft. Ht., P2 = qw*Bx
Note: Loadings P1 and P2 are to be applied per ft. of building height.
Note on K1: "ASCE705W.xls" written by: Alex Tomanovich, P.E.
By
Bx
Bx

## MWFRS (Case 4)
WIND LOADING ANALYSIS - Main Wind-Force Resisting System | [7 empty] | Version 1.4
Per ASCE 7-05 Code Method 2 for Enclosed or Partially Enclosed Buildings
Design Wind Load Case 4 from Figure 6-9
Job Name: |  |  |  | Subject:
Job Number: |  |  |  | Originator: |  |  | Checker:
ASCE 7-05 Figure 6-9 - Design Wind Load Case 4
P2
P1
MT
P1
P2
Application of Additional Torsional Moment
Input Data:
| Bldg. Dimension (x-dir.) = | 100 | ft.
| Bldg. Dimension (y-dir.) = | 200 | ft.
| Windward, Pwx = | 0.029 | ksf
| Leeward, PLx = | 0.008 | ksf
| Windward, Pwy = | 0.0298 | ksf
| Leeward, PLy = | 0.0025 | ksf
Results:
| Length, Bx = | 200 | ft.
| Length, By = | 100 | ft.
| Eccentricity, ex = | 30 | ft., ex = 0.15*Bx
| Eccentricity, ey = | 15 | ft., ey = 0.15*By
| Torsional Moment, MT = | 152.2634 | ft-kips, MT = 0.563*(Pwx+PLx)*Bx*ex + 0.563*(Pwy+PLy)*By*ey
| Perimeter Force, qw = | 0.0038066 | kips/ft./ft. Ht., qw = MT/(2*Bx*By)
| Applied Load, P1 = | 0.38066 | kips/ft. Ht., P1 = qw*By
| Applied Load, P2 = | 0.76132 | kips/ft. Ht., P2 = qw*Bx
Note: Loadings P1 and P2 are to be applied per ft. of building height.
Note on K1: "ASCE705W.xls" written by: Alex Tomanovich, P.E.

## Wall C&C
WIND LOADING ANALYSIS - Wall Components and Cladding | [8 empty] | CALCULATIONS: |  |  |  |  | Version 1.4
Per ASCE 7-05 Code for Buildings of Any Height
Using Method 2: Analytical Procedure (Section 6.5) | [7 empty] | I | Roof Angle, q = | 18.4332 |  | Mean Roof Ht., h = | 36.665
Job Name: |  |  |  | Subject: |  |  |  | II
Job Number: |  |  |  | Originator: |  | Checker: |  | III | GCp Reduction Factor for h <= 60' and q <= 10 deg. = |  |  | 1
IV
Input Data: | [7 empty] | B | Wall Pressure Coefficients, GCp (Fig. 6-11A):
[8 empty] | C | GCp Zone 4 Pos. = | 0.76723
Wind Speed, V = | 90 | mph (Wind Map, Figure 6-1) | [5 empty] | D | GCp Zone 5 Pos. = | 0.76723
Bldg. Classification = | II | (Table 1-1 Occupancy Category) | [5 empty] | Gable | GCp Zone 4 Neg. = | -0.86723
Exposure Category = | C | (Sect. 6.5.6) | [5 empty] | Monoslope | GCp Zone 5 Neg. = | -0.93446
Ridge Height, hr = | 53.33 | ft. (hr >= he) | [5 empty] | Y
Eave Height, he = | 20 | ft. (he <= hr) | [5 empty] | N | Width 'a' for Zone 5 for h <= 60': |  | Width 'a' for Zone 5 for h > 60':
Building Width = | 200 | ft. (Normal to Building Ridge) | [5 empty] | Girt | Lesser of L or B: | 200 | Lesser of L or B: | N.A.
Building Length = | 250 | ft. (Parallel to Building Ridge) | [5 empty] | Siding | 0.1*(L or B): | 20 | 0.1*(L or B): | N.A.
Roof Type = | Gable | (Gable or Monoslope) | [5 empty] | Wall | Compare to 0.4*h: | 14.666 | Compare to 3': | N.A.
Topo. Factor, Kzt = | 1 | (Sect. 6.5.7 & Figure 6-4) | [5 empty] | Fastener | Compare to .04*(L, B): | 14.666 | Use 'a' = | N.A.
Direct. Factor, Kd = | 0.85 | (Table 6-4) | [6 empty] | Compare to 3': | 14.666
Enclosed? (Y/N) | Y | (Sect. 6.2 & Figure 6-5) | [6 empty] | Use 'a' = | 14.666
Hurricane Region? | N
Component Name = | Girt | (Girt, Siding, Wall, or Fastener) | [6 empty] | Positive & Negative Internal Pressure Coefficients, GCpi (Figure 6-5):
Effective Area, Ae = | 208 | ft.^2 (Area Tributary to C&C) | [6 empty] | +GCpi Coef. (PIP) = | 0.18
[9 empty] | -GCpi Coef. (NIP) = | -0.18
Resulting Parameters and Coefficients:
Determine a, zg, Kh, I, and qh:
Roof Angle, q = | 18.4332 | deg. | [6 empty] | a = | 9.5 | (Table 6-2)
Mean Roof Ht., h = | 36.665 | ft. (h = (hr+he)/2, for roof angle >10 deg.) | [6 empty] | zg = | 900 | (Table 6-2)
[9 empty] | Kh = | 1.0246 | (Table 6-3, Case 1a)
Wall External Pressure Coefficients, GCp: | [8 empty] | I = | 1 | (Table 6-1)
GCp Zone 4 Pos. = | 0.76723 | (Fig. 6-11A) | [6 empty] | qh = | 18.0597
GCp Zone 5 Pos. = | 0.76723 | (Fig. 6-11A)
GCp Zone 4 Neg. = | -0.86723 | (Fig. 6-11A)
GCp Zone 5 Neg. = | -0.93446 | (Fig. 6-11A)
Positive & Negative Internal Pressure Coefficients, GCpi (Figure 6-5):
+GCpi Coef. = | 0.18 | (positive internal pressure)
-GCpi Coef. = | -0.18 | (negative internal pressure)
If z <= 15 then: Kz = 2.01*(15/zg)^(2/a) , If z > 15 then: Kz = 2.01*(z/zg)^(2/a) (Table 6-3, Case 1a)
a = | 9.5 | (Table 6-2)
zg = | 900 | (Table 6-2)
Kh = | 1.0246 | (Kh = Kz evaluated at z = h)
I = | 1 | (Table 6-1) | (Importance factor)
Velocity Pressure: qz = 0.00256*Kz*Kzt*Kd*V^2*I (Sect. 6.5.10, Eq. 6-15)
qh = | 18.0597 | psf | qh = 0.00256*Kh*Kzt*Kd*V^2*I (qz evaluated at z = h)
Design Net External Wind Pressures (Sect. 6.5.12.4):
For h <= 60 ft.: p = qh*((GCp) - (+/-GCpi)) (psf)
For h > 60 ft.: p = q*(GCp) - qi*(+/-GCpi) (psf)
where: q = qz for windward walls, q = qh for leeward walls and side walls
qi = qh for all walls (conservatively assumed per Sect. 6.5.12.4.2)
Wind Load Tabulation for Wall Components & Cladding
Component | z | Kh | qh | p = Net Design Pressures (psf) | [10 empty] | User Input for Height, z (ft.):
| (ft.) |  | (psf) | Zone 4 (+) | Zone 4 (-) | Zone 5 (+) | Zone 5 (-) | [7 empty] | N | Use Input Values?
Girt | 0 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
| 15 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
| 20 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
| 25 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
| 30 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
| 35 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
| 40 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
| 45 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
| 50 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
For z = hr: | 53.33 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
For z = he: | 20 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
For z = h: | 36.665 | 1.0246 | 18.0597 | 17.1067 | -18.9127 | 17.1067 | -20.1268
Notes: 1. (+) and (-) signs signify wind pressures acting toward & away from respective surfaces.
2. Width of Zone 5 (end zones), 'a' = |  |  |  | 14.666 | ft.
3. Per Code Section 6.1.4.2, the minimum wind load for C&C shall not be less than 10 psf.
4. References | : a. ASCE 7-05, "Minimum Design Loads for Buildings and Other Structures".
b. "Guide to the Use of the Wind Load Provisions of ASCE 7-05"
by: Kishor C. Mehta and William L. Coulbourne (2010).
Wall Components and Cladding:
Wall Zones for Buildings with h <= 60 ft.
Wall Zones for Buildings with h > 60 ft.
Note on B9: The Basic Design Wind Speed, V (mph), corresponds to a 3-second gust speed at 33' above ground in Exposure Category "C" and is associated with an annual probability of 0.02 of being equaled or exceeded (50-year mean recurrence interval). For Basic Wind Speed Map (Fig. 6-1) see 'Wind Map' worksheet of this workbook.
Note on B10: TABLE 1-1 Occupancy Category of Buildings and Other Structures for Flood, Wind, Snow, Earthquake, and Ice Loads Nature of Occupancy Occupancy Category Buildings and structures that represent a low hazard to human life in the event of failure including, I but not limited to: - Agriculture facilities - Certain temporary facilities - Minor storage facilities Buildings and other structures except those listed in Categories I, III and IV II Buildings and other structures that represent a substantial hazard to human life in the event of III failure including, but not limited to: - Buildings and other structures where more than 300 people congregate in one area - Buildings and other structures with day-care facilities with capacity greater than 150 - Elementary or secondary school facilities with capacity greater than 250 - Colleges & adult education facilities with a capacity greater than 500 - Health care facilities with a capacity greater than 50 resident patients but not having surgery or emergency treatment facilities - Jails and detention facilities Buildings and other structures, not includes in Occupancy Category IV, with potential to cause substantial economic impact and/or mass disruption of day-to-day civilian life in event of failure, including, but not limited to: - Power generating stations, water treatment facilities, sewage treatment facilities, and telecommunication centers - Buildings and structures not included in Category IV containing sufficient quantities of toxic, explosive, or other hazardous materials dangerous to the public if released Buildings and other structures designated as essential facilities including, but not limited to: IV - Hospitals and health care facilities having surgery or emergency treatment facilities - Fire, rescue and police stations and emergency vehicle garages - Designated earthquake, hurricane or other emergency shelters - Designated emergency preparedness, communication, and operation centers and other facilities required for emergency response - Power-generating stations and other public utility facilities required in an emergency - Ancillary structures required for operation of Category IV structures during an emergency - Aviation control towers, air traffic control centers and emergency aircraft hangars - Water storage facilities and pump structures required to maintain water pressure for fire suppression - Buildings and other structures having critical national defense functions - Buildings and structures containing extremely hazardous materials where quantity of material exceeds a threshold quantity established by authority having jurisdiction
Note on B11: Surface Roughness Categories for the purpose of assigning Exposure Category are defined as follows: Surface Roughness "B": Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single family dwellings or larger. Surface Roughness "C": Open terrain with scattered obstructions having heights generally < 30 ft. This category includes flat open country, grass lands, and all water surfaces in hurricane prone regions. Surface Roughness "D": Flat, unobstructed areas and water surfaces outside hurricane prone regions. This category includes smooth mud flats, salt flats, and unbroken ice. Exposure Categories are defined as follows: Exposure "B": Exposure B shall apply where the ground surface roughness condition, as defined by Surface Roughness B, prevails in the upwind direction for a distance of at least 2600 ft. or 20 times the building height, whichever is greater. Exception: For buildings whose mean roof height <= 30 ft., the upwind distance may be reduced to 1500 ft. Exposure "C": Exposure C shall apply for all cases where exposures B and D do not apply. Exposure "D": Exposure D shall apply where the ground surface roughness, as defined by Surface Roughness D, prevails in the upwind direction for a distance >= 5,000 ft. or 20 times the building height, whichever is greater. Exposure D shall extend into downwind areas of Surface Roughness B or C for a distance of 600 ft. or 20 times the height of the building, whichever is greater.
Note on B13: The eave height, 'he', is the distance from the ground surface adjacent to the building to the roof eave line at a particular wall. If the height of the eave varies along the wall, the average height shall be used.
Note on B16: This program assumes that a Gable roof is symmetrical, as the ridge line is assumed in the center of the building width, L. For flat roofs (roof angle = 0 degrees), either Gable or Monoslope may be used.
Note on B17: The Topographic Factor, Kzt, accounts for effect of wind speed-up over isolated hills and escarpments (Sect. 6.5.7 and Fig. 6-4). Kzt = (1+K1*K2*K3)^2 (Eq. 6-3), where: H = height of hill or escarpment relative to the upwind terrain, in feet. Lh = Distance upwind of crest to where the difference in ground elevation is half the height of hill or escarpment, in feet. K1 = factor to account for shape of topographic feature and maximum speed-up effect. K2 = factor to account for reduction in speed-up with distance upwind or downwind of crest. K3 = factor to account for reduction in speed-up with height above local terrain. x = distance (upwind or downwind) from the crest to the building site, in feet. z = height above local ground level, in feet. The effect of wind speed-up shall not be required to be considered (Kzt = 1.0) when H/Lh < 0.2, or H < 15' for Exposures 'C' and 'D', or H < 60' for Exposure 'B'.
Note on B18: Wind Directionality Factor, Kd (Table 6-4) Structure Type Kd Buildings Main Wind-Force Resisting System 0.85 Components and Cladding 0.85 Note: this factor shall only be applied when used in conjunction with load combinations specified in Sect. 2.3 and 2.4. Otherwise, use Kd = 1.0.
Note on B19: This worksheet assumes either Enclosed or Partially Enclosed buildings, and does not consider open buildings. 1. An enclosed building is a building that does not comply with the requirements for open or partially enclosed buildings. 2. An open building is a structure having all walls at least 80% open. 3. A partially enclosed building complies with both of the following conditions: a. the total area of openings in a wall that receives positive external pressure exceeds the sum of the areas of the openings in the balance of the building envelope (walls and roof) by more than 10%; and b. the total area of openings in a wall that receives positive external pressure exceeds 4 sq ft or 1% of the area of that wall, whichever is smaller, and the % of openings in balance of the building envelope does not exceed 20%.
Note on B22: The Effective Area, Ae, for a component or cladding panel equals the span length times the effective width that need not be less than 1/3 of the span length. For a vertically spanning CMU or concrete wall, "Ae" equals the wall height squared divided by 3. For a fastener, the value of "Ae" equals the area tributary to an individual fastener. Note: Major structural components supporting tributary areas > 700 sq ft shall be permitted to be designed using the provisions for main wind-force resisting systems (MWFRS).
Note on B27: The building Mean Roof Height, h, is determined as follows: For buildings with roof angle > 10 degrees: h = (hr+he)/2 For buildings with roof angle <= 10 degrees: h = he
Note on C29: FIG. 6-11A - Walls for Buildings with h <= 60 ft. Positive: Zone 4 & 5 (GCp) = 1.0 for A <= 10 sq.ft. (GCp) = 1.1766-0.1766*logA for 10 < A <= 500 sq.ft. (GCp) = 0.7 for A > 500 sq.ft. Negative: Zone 4 (GCp) = -1.1 for A <= 10 sq.ft. (GCp) = -1.2766+0.1766*logA for 10 < A <= 500 sq.ft. (GCp) = -0.8 for A > 500 sq.ft. Negative: Zone 5 (GCp) = -1.4 for A <= 10 sq.ft. (GCp) = -1.7532+0.3532*logA for 10 < A <= 500 sq.ft. (GCp) = -0.8 for A > 500 sq.ft. FIG. 6-17 - Walls for Buildings with h > 60 ft. Positive: Zone 4 & 5 (GCp) = 0.9 for A <= 20 sq.ft. (GCp) = 1.1792-0.2146*logA for 20 < A <= 500 sq.ft. (GCp) = 0.6 for A > 500 sq.ft. Negative: Zone 4 (GCp) = -0.9 for A <= 20 sq.ft. (GCp) = -1.0861+0.1431*logA for 20 < A <= 500 sq.ft. (GCp) = -0.7 for A > 500 sq.ft. Negative: Zone 5 (GCp) = -1.8 for A <= 20 sq.ft. (GCp) = -2.5445+0.5723*logA for 20 < A <= 500 sq.ft. (GCp) = -1.0 for A > 500 sq.ft.
Note on C39: Terrain Exposure Constants (Table 6-2) Exposure Category a zg (ft) B 7.0 1,200 C 9.5 900 D 11.5 700
Note on C42: Importance Factor, I (Table 6-1): Non-Hurricane Prone Regions Hurricane Prone Regions Category and Hurricane Prone Regions with V > 100 mph with V = 85-100 mph and Alaska I 0.87 0.77 II 1.00 1.00 III 1.15 1.15 IV 1.15 1.15 Note: in the U.S. and its territories hurricane prone regions are defined as: 1. U.S. Atlantic Ocean and Gulf of Mexico coasts where the basic wind speed is > 90 mph. 2. Hawaii, Puerto Rico, Guam, Virgin Islands, and American Samoa.
Note on D46: Per Code Section 6.1.4.1, the minimum wind load to be used in the design of the Main Wind-Force Resisting System shall not be less than 10 psf.
Note on E34: Internal Pressure Coefficients, GCpi (Figure 6-5) Condition (+/-) GCpi Partially enclosed buildings +0.55, -0.55 Enclosed buildings +0.18, -0.18 Per Sect. 6.5.11.1, for a partially enclosed building containing a single, unpartitioned large volume, the GCpi coefficients shall be multiplied by the following reduction factor, Ri: Ri = 1.0 or Ri = 0.5*(1+(1/(1+Vi/(22800*Aog))^0.5)) <= 1.0 where: Aog = total area of openings in the building envelope (walls and roof, ft.^2). Vi = unpartitioned internal volume (ft.^3). Note: This program assumes NO reduction of the GCpi coefficients for large volume buildings. Thus, Ri = 1.0.
Note on E55: Positive (+) pressure applies to windward wall. Maximum positive pressure is evaluated using the positive (+) external wind pressure coefficient, '+GCp', in combination with the negative (-) internal pressure coefficient, '-GCpi'.
Note on F55: Negative (-) pressure applies to leeward wall and side walls. Maximum negative pressure is evaluated using the negative (-) external wind pressure coefficient, '-GCp', in combination with the positive (+) internal pressure coefficient, '+GCpi'.
Note on F86: For h <= 60', width 'a' for Zone 5 is equal to 10% of least horizontal dimension or 0.4*h, whichever is smaller, but not less than either 4% of least horizontal dimension or 3'. For h > 60', width 'a' for Zone 5 is equal to 10% of least horizontal dimension, but not less than 3'.
Note on G55: Positive (+) pressure applies to windward wall. Maximum positive pressure is evaluated using the positive (+) external wind pressure coefficient, '+GCp', in combination with the negative (-) internal pressure coefficient, '-GCpi'.
Note on H3: Note: This program assumes buildings are a maximum of 500 feet tall.
Note on H54: Per Code Section 6.1.4.2, the minimum wind design pressure to be used in the design of components and cladding shall not be less than 10 psf acting in either direction normal to the surface.
Note on H55: Negative (-) pressure applies to leeward wall and side walls. Maximum negative pressure is evaluated using the negative (-) external wind pressure coefficient, '-GCp', in combination with the positive (+) internal pressure coefficient, '+GCpi'.
Note on AA1: "ASCE705W.xls" written by: Alex Tomanovich, P.E.
q o
L
B
hr
he
h
Plan
Elevation
L

## Roof C&C
WIND LOADING ANALYSIS - Roof Components and Cladding | [9 empty] | CALCULATIONS: |  |  |  |  | Version 1.4
Per ASCE 7-05 Code for Bldgs. of Any Height with Gable Roof q <= 45o or Monoslope Roof q <= 3o
Using Method 2: Analytical Procedure (Section 6.5) | [7 empty] | I |  | Roof Angle, q = | 18.4332 |  | Mean Roof Ht., h = | 36.665
Job Name: |  |  |  | Subject: |  |  |  | II
Job Number: |  |  |  | Originator: |  | Checker: |  | III |  | Roof External Pressure Coefficients (without overhangs), GCp:
[8 empty] | IV |  | Fig's. 6-11B, 6-11C, and 6-11D: |  |  | Fig. 6-17 (or Fig. 6-11B):
Input Data: | [7 empty] | B | Fig. 6-11B: | GCp for h <= 60' and q <= 7: |  |  | GCp for h > 60' and q <= 10:
[8 empty] | C |  | For Zone 1,2,3 Pos. = | N.A. |  | For Zone 1,2,3 Pos. = | N.A.
Wind Speed, V = | 90 | mph (Wind Map, Figure 6-1) | [5 empty] | D |  | For Zone 1 Neg. = | N.A. |  | For Zone 1 Neg. = | N.A.
Bldg. Classification = | II | (Table 1-1 Occupancy Category) | [5 empty] | Gable |  | For Zone 2 Neg. = | N.A. |  | For Zone 2 Neg. = | N.A.
Exposure Category = | C | (Sect. 6.5.6) | [5 empty] | Monoslope |  | For Zone 3 Neg. = | N.A. |  | For Zone 3 Neg. = | N.A.
Ridge Height, hr = | 53.33 | ft. (hr >= he) | [5 empty] | Y | Fig. 6-11C: | GCp for h <= 60' and 7 < q <= 27: |  |  | GCp for h > 60' and 10 < q <= 27:
Eave Height, he = | 20 | ft. (he <= hr) | [5 empty] | N |  | For Zone 1,2,3 Pos. = | 0.3 |  | For Zone 1,2,3 Pos. = | N.A.
Building Width = | 200 | ft. (Normal to Building Ridge) | [5 empty] | Purlin |  | For Zone 1 Neg. = | -0.8 |  | For Zone 1 Neg. = | N.A.
Building Length = | 250 | ft. (Parallel to Building Ridge) | [5 empty] | Joist |  | For Zone 2 Neg. = | -1.2 |  | For Zone 2 Neg. = | N.A.
Roof Type = | Gable | (Gable or Monoslope) | [5 empty] | Decking |  | For Zone 3 Neg. = | -2 |  | For Zone 3 Neg. = | N.A.
Topo. Factor, Kzt = | 1 | (Sect. 6.5.7 & Figure 6-4) | [5 empty] | Fastener | Fig. 6-11D: | GCp for h <= 60' and 27 < q <= 45: |  |  | GCp for h > 60' and 27 < q <= 45:
Direct. Factor, Kd = | 0.85 | (Table 6-4) | [7 empty] | For Zone 1,2,3 Pos. = | N.A. |  | For Zone 1,2,3 Pos. = | N.A.
Enclosed? (Y/N) | Y | (Sect. 6.2 & Figure 6-5) | [7 empty] | For Zone 1 Neg. = | N.A. |  | For Zone 1 Neg. = | N.A.
Hurricane Region? | N | [8 empty] | For Zone 2 Neg. = | N.A. |  | For Zone 2 Neg. = | N.A.
Component Name = | Joist | (Purlin, Joist, Decking, or Fastener) | [7 empty] | For Zone 3 Neg. = | N.A. |  | For Zone 3 Neg. = | N.A.
Effective Area, Ae = | 208 | ft.^2 (Area Tributary to C&C) | [7 empty] | Use Zone 1,2,3 Pos. = | 0.3 |  | Use Zone 1,2,3 Pos. = | N.A.
Overhangs? (Y/N) | N | (if used, overhangs on all sides) | [7 empty] | Use Zone 1 Neg. = | -0.8 |  | Use Zone 1 Neg. = | N.A.
[10 empty] | Use Zone 2 Neg. = | -1.2 |  | Use Zone 2 Neg. = | N.A.
Resulting Parameters and Coefficients: | [9 empty] | Use Zone 3 Neg. = | -2 |  | Use Zone 3 Neg. = | N.A.
Roof Angle, q = | 18.4332 | deg. | [7 empty] | Roof External Pressure Coefficients (with overhangs), GCp:
Mean Roof Ht., h = | 36.665 | ft. (h = (hr+he)/2, for roof angle >10 deg.) | [7 empty] | Fig's. 6-11B, 6-11C, and 6-11D: |  |  | Fig. 6-17 (or Fig. 6-11B):
[9 empty] | Fig. 6-11B: | GCp for h <= 60' and q <= 7: |  |  | GCp for h > 60' and q <= 10:
Roof External Pressure Coefficients, GCp: | [9 empty] | For Zone 1,2,3 Pos. = | N.A. |  | For Zone 1,2,3 Pos. = | N.A.
GCp Zone 1-3 Pos. = | 0.3 | (Fig. 6-11B thru 6-11D) | [7 empty] | For Zone 1 Neg. = | N.A. |  | For Zone 1 Neg. = | N.A.
GCp Zone 1 Neg. = | -0.8 | (Fig. 6-11B thru 6-11D) | [7 empty] | For Zone 2 Neg. = | N.A. |  | For Zone 2 Neg. = | N.A.
GCp Zone 2 Neg. = | -1.2 | (Fig. 6-11B thru 6-11D) | [7 empty] | For Zone 3 Neg. = | N.A. |  | For Zone 3 Neg. = | N.A.
GCp Zone 3 Neg. = | -2 | (Fig. 6-11B thru 6-11D) | [6 empty] | Fig. 6-11C: | GCp for h <= 60' and 7 < q <= 27: |  |  | GCp for h > 60' and 10 < q <= 27:
Positive & Negative Internal Pressure Coefficients, GCpi (Figure 6-5): | [9 empty] | For Zone 1,2,3 Pos. = | N.A. |  | For Zone 1,2,3 Pos. = | N.A.
+GCpi Coef. = | 0.18 | (positive internal pressure) | [7 empty] | For Zone 1 Neg. = | N.A. |  | For Zone 1 Neg. = | N.A.
-GCpi Coef. = | -0.18 | (negative internal pressure) | [7 empty] | For Zone 2 Neg. = | N.A. |  | For Zone 2 Neg. = | N.A.
If z <= 15 then: Kz = 2.01*(15/zg)^(2/a) , If z > 15 then: Kz = 2.01*(z/zg)^(2/a) (Table 6-3, Case 1a) | [9 empty] | For Zone 3 Neg. = | N.A. |  | For Zone 3 Neg. = | N.A.
a = | 9.5 | [7 empty] | Fig. 6-11D: | GCp for h <= 60' and 27 < q <= 45: |  |  | GCp for h > 60' and 27 < q <= 45:
zg = | 900 | (Table 6-2) | [7 empty] | For Zone 1,2,3 Pos. = | N.A. |  | For Zone 1,2,3 Pos. = | N.A.
Kh = | 1.0246 | (Kh = Kz evaluated at z = h) | [7 empty] | For Zone 1 Neg. = | N.A. |  | For Zone 1 Neg. = | N.A.
I = | 1 | (Table 6-1) | (Importance factor) | [6 empty] | For Zone 2 Neg. = | N.A. |  | For Zone 2 Neg. = | N.A.
Velocity Pressure: qz = 0.00256*Kz*Kzt*Kd*V^2*I (Sect. 6.5.10, Eq. 6-15) | [9 empty] | For Zone 3 Neg. = | N.A. |  | For Zone 3 Neg. = | N.A.
qh = | 18.0597 | psf | qh = 0.00256*Kh*Kzt*Kd*V^2*I (qz evaluated at z = h) | [6 empty] | Use Zone 1,2,3 Pos. = | N.A. |  | Use Zone 1,2,3 Pos. = | N.A.
[10 empty] | Use Zone 1 Neg. = | N.A. |  | Use Zone 1 Neg. = | N.A.
Design Net External Wind Pressures (Sect. 6.5.12.4): | [9 empty] | Use Zone 2 Neg. = | N.A. |  | Use Zone 2 Neg. = | N.A.
For h <= 60 ft.: p = qh*((GCp) - (+/-GCpi)) (psf) | [9 empty] | Use Zone 3 Neg. = | N.A. |  | Use Zone 3 Neg. = | N.A.
For h > 60 ft.: p = q*(GCp) - qi*(+/-GCpi) (psf)
where: q = qh for roof
qi = qh for roof (conservatively assumed per Sect. 6.5.12.4.2)
[10 empty] | Width 'a' for Zone 2 for h <= 60': |  |  | Width 'a' for Zone 2 for h > 60':
[10 empty] | Lesser of L or B: | 200 |  | Lesser of L or B: | N.A.
Wind Load Tabulation for Roof Components & Cladding | [9 empty] | 0.1*(L or B): | 20 |  | 0.1*(L or B): | N.A.
Component | z | Kh | qh | p = Net Design Pressures (psf) | [5 empty] | Compare to 0.4*h: | 14.666 |  | Compare to 3': | N.A. |  | User Input for Height, z (ft.):
| (ft.) |  | (psf) | Zone 1,2,3 (+) | Zone 1 (-) | Zone 2 (-) | Zone 3 (-) |  |  | Compare to .04*(L, B): | 14.666 |  | Use 'a' = | N.A. |  | N | Use Input Values?
Joist | 0 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701 |  |  | Compare to 3': | 14.666
| 15 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701 |  |  | Use 'a' = | 14.666
| 20 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701
| 25 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701 |  |  | Positive & Negative Internal Pressure Coefficients, GCpi (Figure 6-5):
| 30 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701 |  |  | +GCpi Coef. (PIP) = | 0.18
| 35 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701 |  |  | -GCpi Coef. (NIP) = | -0.18
| 40 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701
| 45 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701 |  |  | Determine a, zg, Kh, I, and qh:
| 50 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701 |  |  | a = | 9.5 | (Table 6-2)
For z = hr: | 53.33 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701 |  |  | zg = | 900 | (Table 6-2)
[10 empty] | Kh = | 1.0246 | (Table 6-3, Case 1a)
[10 empty] | I = | 1 | (Table 6-1)
[10 empty] | qh = | 18.0597
For z = he: | 20 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701
For z = h: | 36.665 | 1.0246 | 18.0597 | 8.6687 | -17.6985 | -24.9224 | -39.3701
Notes: 1. (+) and (-) signs signify wind pressures acting toward & away from respective surfaces.
2. Width of Zone 2 (edge), 'a' = |  |  | 14.666 | ft.
3. Width of Zone 3 (corner), 'a' = |  |  | 14.666 | ft.
4. For monoslope roofs with q <= 3 degrees, use Fig. 6-11B for 'GCp' values with 'qh'.
5. For buildings with h > 60' and q > 10 degrees, use Fig. 6-17 for 'GCp' values with 'qh'.
6. For all buildings with overhangs, use Fig. 6-11B, C, and D for 'GCp' values per Sect. 6.5.11.4.2.
7. If a parapet >= 3' in height is provided around perimeter of roof with q <= 10 degrees,
Zone 3 shall be treated as Zone 2.
8. Per Code Section 6.1.4.2, the minimum wind load for C&C shall not be less than 10 psf.
9. References | : a. ASCE 7-05, "Minimum Design Loads for Buildings and Other Structures".
b. "Guide to the Use of the Wind Load Provisions of ASCE 7-05"
by: Kishor C. Mehta and William L. Coulbourne (2010).
Roof Components and Cladding:
q <= 7 deg. |  | 7 deg. < q <= 27 deg. |  |  | 27 deg. < q <= 45 deg.
Roof Zones for Buildings with h <= 60 ft.
(for Gable Roofs <= 45o and Monoslope Roofs <= 3o)
Roof Zones for Buildings with h > 60 ft.
(for Gable Roofs <= 10o and Monoslope Roofs <= 3o)
Note on B9: The Basic Design Wind Speed, V (mph), corresponds to a 3-second gust speed at 33' above ground in Exposure Category "C" and is associated with an annual probability of 0.02 of being equaled or exceeded (50-year mean recurrence interval). For Basic Wind Speed Map (Fig. 6-1) see 'Wind Map' worksheet of this workbook.
Note on B10: TABLE 1-1 Occupancy Category of Buildings and Other Structures for Flood, Wind, Snow, Earthquake, and Ice Loads Nature of Occupancy Occupancy Category Buildings and structures that represent a low hazard to human life in the event of failure including, I but not limited to: - Agriculture facilities - Certain temporary facilities - Minor storage facilities Buildings and other structures except those listed in Categories I, III and IV II Buildings and other structures that represent a substantial hazard to human life in the event of III failure including, but not limited to: - Buildings and other structures where more than 300 people congregate in one area - Buildings and other structures with day-care facilities with capacity greater than 150 - Elementary or secondary school facilities with capacity greater than 250 - Colleges & adult education facilities with a capacity greater than 500 - Health care facilities with a capacity greater than 50 resident patients but not having surgery or emergency treatment facilities - Jails and detention facilities Buildings and other structures, not includes in Occupancy Category IV, with potential to cause substantial economic impact and/or mass disruption of day-to-day civilian life in event of failure, including, but not limited to: - Power generating stations, water treatment facilities, sewage treatment facilities, and telecommunication centers - Buildings and structures not included in Category IV containing sufficient quantities of toxic, explosive, or other hazardous materials dangerous to the public if released Buildings and other structures designated as essential facilities including, but not limited to: IV - Hospitals and health care facilities having surgery or emergency treatment facilities - Fire, rescue and police stations and emergency vehicle garages - Designated earthquake, hurricane or other emergency shelters - Designated emergency preparedness, communication, and operation centers and other facilities required for emergency response - Power-generating stations and other public utility facilities required in an emergency - Ancillary structures required for operation of Category IV structures during an emergency - Aviation control towers, air traffic control centers and emergency aircraft hangars - Water storage facilities and pump structures required to maintain water pressure for fire suppression - Buildings and other structures having critical national defense functions - Buildings and structures containing extremely hazardous materials where quantity of material exceeds a threshold quantity established by authority having jurisdiction
Note on B11: Surface Roughness Categories for the purpose of assigning Exposure Category are defined as follows: Surface Roughness "B": Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single family dwellings or larger. Surface Roughness "C": Open terrain with scattered obstructions having heights generally < 30 ft. This category includes flat open country, grass lands, and all water surfaces in hurricane prone regions. Surface Roughness "D": Flat, unobstructed areas and water surfaces outside hurricane prone regions. This category includes smooth mud flats, salt flats, and unbroken ice. Exposure Categories are defined as follows: Exposure "B": Exposure B shall apply where the ground surface roughness condition, as defined by Surface Roughness B, prevails in the upwind direction for a distance of at least 2600 ft. or 20 times the building height, whichever is greater. Exception: For buildings whose mean roof height <= 30 ft., the upwind distance may be reduced to 1500 ft. Exposure "C": Exposure C shall apply for all cases where exposures B and D do not apply. Exposure "D": Exposure D shall apply where the ground surface roughness, as defined by Surface Roughness D, prevails in the upwind direction for a distance >= 5,000 ft. or 20 times the building height, whichever is greater. Exposure D shall extend into downwind areas of Surface Roughness B or C for a distance of 600 ft. or 20 times the height of the building, whichever is greater.
Note on B13: The eave height, 'he', is the distance from the ground surface adjacent to the building to the roof eave line at a particular wall. If the height of the eave varies along the wall, the average height shall be used.
Note on B16: This program assumes that a Gable roof is symmetrical, as the ridge line is assumed in the center of the building width, L. For flat roofs (roof angle = 0 degrees), either Gable or Monoslope may be used.
Note on B17: The Topographic Factor, Kzt, accounts for effect of wind speed-up over isolated hills and escarpments (Sect. 6.5.7 and Fig. 6-4). Kzt = (1+K1*K2*K3)^2 (Eq. 6-3), where: H = height of hill or escarpment relative to the upwind terrain, in feet. Lh = Distance upwind of crest to where the difference in ground elevation is half the height of hill or escarpment, in feet. K1 = factor to account for shape of topographic feature and maximum speed-up effect. K2 = factor to account for reduction in speed-up with distance upwind or downwind of crest. K3 = factor to account for reduction in speed-up with height above local terrain. x = distance (upwind or downwind) from the crest to the building site, in feet. z = height above local ground level, in feet. The effect of wind speed-up shall not be required to be considered (Kzt = 1.0) when H/Lh < 0.2, or H < 15' for Exposures 'C' and 'D', or H < 60' for Exposure 'B'.
Note on B18: Wind Directionality Factor, Kd (Table 6-4) Structure Type Kd Buildings Main Wind-Force Resisting System 0.85 Components and Cladding 0.85 Note: this factor shall only be applied when used in conjunction with load combinations specified in Sect. 2.3 and 2.4. Otherwise, use Kd = 1.0.
Note on B19: This worksheet assumes either Enclosed or Partially Enclosed buildings, and does not consider open buildings. 1. An enclosed building is a building that does not comply with the requirements for open or partially enclosed buildings. 2. An open building is a structure having all walls at least 80% open. 3. A partially enclosed building complies with both of the following conditions: a. the total area of openings in a wall that receives positive external pressure exceeds the sum of the areas of the openings in the balance of the building envelope (walls and roof) by more than 10%; and b. the total area of openings in a wall that receives positive external pressure exceeds 4 sq ft or 1% of the area of that wall, whichever is smaller, and the % of openings in balance of the building envelope does not exceed 20%.
Note on B22: The Effective Area, Ae, for a component or cladding panel equals the span length times the effective width that need not be less than 1/3 of the span length; however, for a fastener it is the area tributary to an individual fastener. Note: Major structural components supporting tributary areas > 700 sq ft shall be permitted to be designed using the provisions for main wind-force resisting systems (MWFRS).
Note on B28: The building Mean Roof Height, h, is determined as follows: For buildings with roof angle > 10 degrees: h = (hr+he)/2 For buildings with roof angle <= 10 degrees: h = he
Note on C40: Terrain Exposure Constants (Table 6-2) Exposure Category a zg (ft) B 7.0 1,200 C 9.5 900 D 11.5 700
Note on C42: Importance Factor, I (Table 6-1): Non-Hurricane Prone Regions Hurricane Prone Regions Category and Hurricane Prone Regions with V > 100 mph with V = 85-100 mph and Alaska I 0.87 0.77 II 1.00 1.00 III 1.15 1.15 IV 1.15 1.15 Note: in the U.S. and its territories hurricane prone regions are defined as: 1. U.S. Atlantic Ocean and Gulf of Mexico coasts where the basic wind speed is > 90 mph. 2. Hawaii, Puerto Rico, Guam, Virgin Islands, and American Samoa.
Note on D46: Per Code Section 6.1.4.1, the minimum wind load to be used in the design of the Main Wind-Force Resisting System shall not be less than 10 psf.
Note on E31: FIG. 6-11B - Roofs for Buildings with h <= 60 ft. For q <= 7: Positive without overhang: Zone 1,2,3 (GCp) = 0.3 for A <= 10 sq.ft. (GCp) = 0.4000-0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = 0.2 for A > 100 sq.ft. Negative without overhang: Zone 1 (GCp) = -1.0 for A <= 10 sq.ft. (GCp) = -1.1000+0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = -0.9 for A > 100 sq.ft. Negative without overhang: Zone 2 (GCp) = -1.8 for A <= 10 sq.ft. (GCp) = -2.5000+0.7000*logA for 10 < A <= 100 sq.ft. (GCp) = -1.1 for A > 100 sq.ft. Negative without overhang: Zone 3 (GCp) = -2.8 for A <= 10 sq.ft. (GCp) = -4.5000+1.7000*logA for 10 < A <= 100 sq.ft. (GCp) = -1.1 for A > 100 sq.ft.
Note on E32: FIG. 6-11C - Roofs for Buildings with h <= 60 ft. For 7 < q <= 27: Positive without overhang: Zone 1,2,3 (GCp) = 0.5 for A <= 10 sq.ft. (GCp) = 0.7000-0.2000*logA for 10 < A <= 100 sq.ft. (GCp) = 0.3 for A > 100 sq.ft. Negative without overhang: Zone 1 (GCp) = -0.9 for A <= 10 sq.ft. (GCp) = -1.0000+0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = -0.8 for A > 100 sq.ft. Negative without overhang: Zone 2 (GCp) = -1.7 for A <= 10 sq.ft. (GCp) = -2.6+.5*logA for 10 < A <= 100 sq.ft. (GCp) = -1.2 for A > 100 sq.ft. Negative without overhang: Zone 3 (GCp) = -2.6 for A <= 10 sq.ft. (GCp) = -3.2000+0.6000*logA for 10 < A <= 100 sq.ft. (GCp) = -2.0 for A > 100 sq.ft.
Note on E33: FIG. 6-11D - Roofs for Buildings with h <= 60 ft. For 27 < q <= 45: Positive without overhang: Zone 1,2,3 (GCp) = 0.9 for A <= 10 sq.ft. (GCp) = 1.0000-0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = 0.8 for A > 100 sq.ft. Negative without overhang: Zone 1 (GCp) = -1.0 for A <= 10 sq.ft. (GCp) = -1.2000+0.2000*logA for 10 < A <= 100 sq.ft. (GCp) = -0.8 for A > 100 sq.ft. Negative without overhang: Zone 2 & 3 (GCp) = -1.2 for A <= 10 sq.ft. (GCp) = -1.4000+0.2000*logA for 10 < A <= 100 sq.ft. (GCp) = -1.0 for A > 100 sq.ft.
Note on E35: Internal Pressure Coefficients, GCpi (Figure 6-5) Condition (+/-) GCpi Partially enclosed buildings +0.55, -0.55 Enclosed buildings +0.18, -0.18 Per Sect. 6.5.11.1, for a partially enclosed building containing a single, unpartitioned large volume, the GCpi coefficients shall be multiplied by the following reduction factor, Ri: Ri = 1.0 or Ri = 0.5*(1+(1/(1+Vi/(22800*Aog))^0.5)) <= 1.0 where: Aog = total area of openings in the building envelope (walls and roof, ft.^2). Vi = unpartitioned internal volume (ft.^3). Note: This program assumes NO reduction of the GCpi coefficients for large volume buildings. Thus, Ri = 1.0.
Note on E86: For h <= 60', width 'a' for Zone 2 is equal to 10% of least horizontal dimension or 0.4*h, whichever is smaller, but not less than either 4% of least horizontal dimension or 3'. For h > 60', width 'a' for Zone 2 is equal to 10% of least horizontal dimension, but not less than 3'.
Note on F31: FIG. 6-11B - Roofs for Buildings with h <= 60 ft. For q <= 7: Positive with overhang: Zone 1,2,3 (GCp) = 0.3 for A <= 10 sq.ft. (GCp) = 0.4000-0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = 0.2 for A > 100 sq.ft. Negative with overhang: Zone 1 & 2 (GCp) = -1.7 for A <= 10 sq.ft. (GCp) = -1.8000+0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = -3.0307+0.7153*logA for 100 < A <= 500 sq.ft. (GCp) = -1.1 for A > 500 sq.ft. Negative with overhang: Zone 3 (GCp) = -2.8 for A <= 10 sq.ft. (GCp) = -4.8000+2.0000*logA for 10 < A <= 100 sq.ft. (GCp) = -0.8 for A > 100 sq.ft.
Note on F32: FIG. 6-11C - Roofs for Buildings with h <= 60 ft. For 7 < q <= 27: Positive with overhang: Zone 1,2,3 (GCp) = 0.5 for A <= 10 sq.ft. (GCp) = 0.7000-0.2000*logA for 10 < A <= 100 sq.ft. (GCp) = 0.3 for A > 100 sq.ft. Negative with overhang: Zone 1 (GCp) = -0.9 for A <= 10 sq.ft. (GCp) = -1.0000+0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = -0.8 for A > 100 sq.ft. Negative with overhang: Zone 2 (GCp) = -2.2 for All A Negative with overhang: Zone3 (GCp) = -3.7 for A <= 10 sq.ft. (GCp) = -4.9+1.2*logA for 10 < A <= 100 sq.ft. (GCp) = -2.5 for A > 100 sq.ft.
Note on F33: FIG. 6-11D - Roofs for Buildings with h <= 60 ft. For 27 < q <= 45: Positive with overhang: Zone 1,2,3 (GCp) = 0.9 for A <= 10 sq.ft. (GCp) = 1.0000-0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = 0.8 for A > 100 sq.ft. Negative with overhang: Zone 1 (GCp) = -1.0 for A <= 10 sq.ft. (GCp) = -1.2000+0.2000*logA for 10 < A <= 100 sq.ft. (GCp) = -0.8 for A > 100 sq.ft. Negative with overhang: Zone 2 & 3 (GCp) = -2.0 for A <= 10 sq.ft. (GCp) = -2.2+0.2*logA for 10 < A <= 100 sq.ft. (GCp) = -1.8 for A > 100 sq.ft.
Note on G31: FIG. 6-17 - Roofs for Buildings with h > 60 ft. Note: for q > 10, use FIG. 6-11C and 6-11D For q <= 10: Negative without overhang: Zone 1 (GCp) = -1.4 for A <= 10 sq.ft. (GCp) = -1.6943-0.2943*logA for 10 < A <= 500 sq.ft. (GCp) = -0.9 for A > 500 sq.ft. Negative without overhang: Zone 2 (GCp) = -2.3 for A <= 10 sq.ft. (GCp) = -2.7120+0.4120*logA for 10 < A <= 500 sq.ft. (GCp) = -1.6 for A > 500 sq.ft. Negative without overhang: Zone 3 (GCp) = -3.2 for A <= 10 sq.ft. (GCp) = -3.7297+0.5297*logA for 10 < A <= 500 sq.ft. (GCp) = -2.3 for A > 500 sq.ft.
Note on G32: FIG. 6-17 - Roofs for Buildings with h > 60 ft. Note: for q > 10, use FIG. 6-11C and 6-11D For 10 < q <= 30: Positive without overhang: Zone 1,2,3 (GCp) = 0.5 for A <= 10 sq.ft. (GCp) = 0.7000-0.2000*logA for 10 < A <= 100 sq.ft. (GCp) = 0.3 for A > 100 sq.ft. Negative without overhang: Zone 1 (GCp) = -0.9 for A <= 10 sq.ft. (GCp) = -1.0000+0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = -0.8 for A > 100 sq.ft. Negative without overhang: Zone 2 (GCp) = -1.7 for A <= 10 sq.ft. (GCp) = -2.6+.5*logA for 10 < A <= 100 sq.ft. (GCp) = -1.2 for A > 100 sq.ft. Negative without overhang: Zone 3 (GCp) = -2.6 for A <= 10 sq.ft. (GCp) = -3.2000+0.6000*logA for 10 < A <= 100 sq.ft. (GCp) = -2.0 for A > 100 sq.ft.
Note on G33: FIG. 6-17 - Roofs for Buildings with h > 60 ft. Note: for q > 10, use FIG. 6-11C and 6-11D For 30 < q <= 45: Positive without overhang: Zone 1,2,3 (GCp) = 0.9 for A <= 10 sq.ft. (GCp) = 1.0000-0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = 0.8 for A > 100 sq.ft. Negative without overhang: Zone 1 (GCp) = -1.0 for A <= 10 sq.ft. (GCp) = -1.2000+0.2000*logA for 10 < A <= 100 sq.ft. (GCp) = -0.8 for A > 100 sq.ft. Negative without overhang: Zone 2 & 3 (GCp) = -1.2 for A <= 10 sq.ft. (GCp) = -1.4000+0.2000*logA for 10 < A <= 100 sq.ft. (GCp) = -1.0 for A > 100 sq.ft.
Note on H3: Note: This program assumes buildings are a maximum of 500 feet tall.
Note on H31: FIG. 6-17 - Roofs for Buildings with h > 60 ft. Note: for all buildings with overhangs, use FIG. 6-11B thru 6-11D For q <= 10: Positive with overhang: Zone 1,2,3 (GCp) = 0.3 for A <= 10 sq.ft. (GCp) = 0.4000-0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = 0.2 for A > 100 sq.ft. Negative with overhang: Zone 1 & 2 (GCp) = -1.7 for A <= 10 sq.ft. (GCp) = -1.8000+0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = -3.0307+0.7153*logA for 100 < A <= 500 sq.ft. (GCp) = -1.1 for A > 500 sq.ft. Negative with overhang: Zone 3 (GCp) = -2.8 for A <= 10 sq.ft. (GCp) = -4.8000+2.0000*logA for 10 < A <= 100 sq.ft. (GCp) = -0.8 for A > 100 sq.ft.
Note on H32: FIG. 6-17 - Roofs for Buildings with h > 60 ft. Note: for all buildings with overhangs, use FIG. 6-11B thru 6-11D For 10 < q <= 30: Positive with overhang: Zone 1,2,3 (GCp) = 0.5 for A <= 10 sq.ft. (GCp) = 0.7000-0.2000*logA for 10 < A <= 100 sq.ft. (GCp) = 0.3 for A > 100 sq.ft. Negative with overhang: Zone 1 (GCp) = -0.9 for A <= 10 sq.ft. (GCp) = -1.0000+0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = -0.8 for A > 100 sq.ft. Negative with overhang: Zone 2 (GCp) = -2.2 for All A Negative with overhang: Zone3 (GCp) = -3.7 for A <= 10 sq.ft. (GCp) = -4.9+1.2*logA for 10 < A <= 100 sq.ft. (GCp) = -2.5 for A > 100 sq.ft.
Note on H33: FIG. 6-17 - Roofs for Buildings with h > 60 ft. Note: for all buildings with overhangs, use FIG. 6-11B thru 6-11D For 30 < q <= 45: Positive with overhang: Zone 1,2,3 (GCp) = 0.9 for A <= 10 sq.ft. (GCp) = 1.0000-0.1000*logA for 10 < A <= 100 sq.ft. (GCp) = 0.8 for A > 100 sq.ft. Negative with overhang: Zone 1 (GCp) = -1.0 for A <= 10 sq.ft. (GCp) = -1.2000+0.2000*logA for 10 < A <= 100 sq.ft. (GCp) = -0.8 for A > 100 sq.ft. Negative with overhang: Zone 2 & 3 (GCp) = -2.0 for A <= 10 sq.ft. (GCp) = -2.2+0.2*logA for 10 < A <= 100 sq.ft. (GCp) = -1.8 for A > 100 sq.ft.
Note on H54: Per Code Section 6.1.4.2, the minimum wind design pressure to be used in the design of components and cladding shall not be less than 10 psf acting in either direction normal to the surface.
Note on AA1: "ASCE705W.xls" written by: Alex Tomanovich, P.E.
q o
L
B
hr
he
h
Plan
Elevation
L

## Stacks & Tanks
WIND LOADING ANALYSIS - Chimneys, Stacks, and Vertical Tanks | [11 empty] | CALCULATIONS: |  |  | Version 1.4
Per ASCE 7-05 Code for Cantilevered Structures Classified as Other Structures
[10 empty] | I |  | Ratio of h/D = | 20 |  |  | Force Coefficients for Chimneys, Tanks, and Similar Structures, Cf (Figure 6-21):
Job Name: |  |  |  |  | Subject: |  |  |  |  | II |  | Cf for Square = | N.A. | for all surfaces and wind normal to face |  | Cross-Section |  |  | Type of Surface | Cf for h/D Values of:
Job Number: |  |  |  |  | Originator: |  |  | Checker: |  | III |  | Cf for Square = | N.A. | for all surfaces and wind along diagonal | [5 empty] | 1 | 7 | 25
[10 empty] | IV |  | Cf for Hexagon = | N.A. | for all surfaces |  | Square (wind normal to face) |  |  | All | 1.3 | 1.4 | 2
Input Data: | [9 empty] | B |  | Cf for Octagon = | N.A. | for all surfaces |  | Square (wind along diagonal) |  |  | All | 1 | 1.1 | 1.5
[10 empty] | C |  | Cf for Round = | 0.67222 | for moderately smooth surface (D'/D<0.02) and D*SQRT(qz)>2.5 |  | Hexagonal or Octagonal |  |  | All | 1 | 1.2 | 1.4
V = | 90 | mph (Wind Map, Figure 6-1) | [7 empty] | D |  | Cf for Round = | 0.87222 | for rough surface (D'/D=0.02) and D*SQRT(qz)>2.5 |  | Round (D*SQRT(qz)>2.5) |  |  | 1-Moderately Smooth | 0.5 | 0.6 | 0.7
Class. = | II | (Occupancy Category from Table 1-1) | [7 empty] | Round |  | Cf for Round = | 1.1444 | for very rough surface (D'/D>=0.08) and D*SQRT(qz)>2.5 |  |  |  |  | 2-Rough (D'/D=0.02) | 0.7 | 0.8 | 0.9
Exposure = | B | (Exposure Category from Sect. 6.5.6) | [7 empty] | Hexagon |  | Cf for Round = | 1.0889 | for all surfaces and D*SQRT(qz)<=2.5 |  |  |  |  | 3-Very Rough (D'/D=0.08) | 0.8 | 1 | 1.2
Kzt = | 1 | (Topographic Factor from Sect. 6.5.7) | [7 empty] | Octagon | [5 empty] | Round (D*SQRT(qz)<=2.5) |  |  | 4-All | 0.7 | 0.8 | 1.2
h = | 80 | ft. (Height of Vessel itself) | [7 empty] | Square |  | Determine a, zg, I:
Hb = | 50 | ft. (Height of Vessel Base Above Ground) | [7 empty] | Normal |  | a = | 7 | (Table 6-2) |  | Wind Direction = | Normal | (applicable for square cross-section only)
Outside D = | 4 | ft. (Diameter or Width of Surface Normal to Wind) | [7 empty] | Diagonal |  | zg = | 1200 | (Table 6-2) |  | D' = | 1 | ft. (depth of protruding elements)
t = | 0.375 | in. (Wall Thickness of Vessel) | [7 empty] | Y |  | I = | 1 | (Table 6-1) |  | D'/D = | 0.25
gt = | 490 | pcf (Vessel Material Unit Weight) | [5 empty] | Elevation |  | N | [5 empty] | Type Round Surface = | 3 | Very Rough
Shape? | Round | (Round, Hexagon, Octagon, or Square) | [9 empty] | Base Shear and Moment Tabulation |  |  |  | h/D = | 20
b = | 0.01 | (Damping Ratio = 0.010-0.070) | [9 empty] | for trapezoidal pressure distribution: |  |  |  | D*SQRT(qz) = | 15.9849 | > 2.5
Kd = | 0.95 | (Direct. Factor, Table 6-4) |  |  | Wind Load Tabulation for Stack / Tank | [6 empty] | Tributary Cant. | Tributary Cant. |  |  | Cf = | 1.1444 | (interpolated Force Coefficient from Figure 6-21 above)
Cf = | 0.75 | (Force Coef. from Fig. 6-21) |  |  | z | Kz | qz | p=qz*G*Cf | F=qz*G*Cf*D |  |  | Base Shear: | Base Moment:
Hurricane? | N |  |  |  | (ft.) |  | (psf) | (psf) | (lb/ft) |  | for rectangular, stepped distribution: | (kips/segment) | (ft-kips/segment) | for rectangular, stepped distribution: |  | Note: if applicable, user may input above value of 'Cf' into cell B21.
[5 empty] | 50 | 0.81068 | 15.9698 | 10.1807 | 40.7229 |  | 0 | 0 | 0 | 0
[5 empty] | 55 | 0.83306 | 16.4106 | 10.4618 | 41.8471 |  | 0.20924 | 0.20642 | 0.5184 | 0.52309
Resulting Parameters and Coefficients: |  |  |  |  | 60 | 0.85403 | 16.8237 | 10.7251 | 42.9005 |  | 0.2145 | 0.21187 | 1.5912 | 1.6088
[5 empty] | 65 | 0.87379 | 17.2129 | 10.9732 | 43.8929 |  | 0.21946 | 0.21698 | 2.7144 | 2.7433
If z < 15 then: Kz = 2.01*(15/zg)^(2/a) |  |  |  |  | 70 | 0.89248 | 17.5812 | 11.208 | 44.8322 |  | 0.22416 | 0.22181 | 3.8837 | 3.9228
If z >= 15 then: Kz = 2.01*(z/zg)^(2/a) |  |  |  |  | 75 | 0.91025 | 17.9312 | 11.4312 | 45.7247 |  | 0.22862 | 0.22639 | 5.0957 | 5.144
a = | 7 | (Table 6-2) |  |  | 80 | 0.92719 | 18.265 | 11.6439 | 46.5756 |  | 0.23288 | 0.23075 | 6.3474 | 6.4041
zg = | 1200 | (Table 6-2) |  |  | 85 | 0.94339 | 18.5841 | 11.8474 | 47.3894 |  | 0.23695 | 0.23491 | 7.6364 | 7.7008
I = | 1 | (Table 6-1) | (Import. Factor) |  | 90 | 0.95893 | 18.8901 | 12.0424 | 48.1697 |  | 0.24085 | 0.2389 | 8.9603 | 9.0318
h/D = | 20 |  |  |  | 95 | 0.97385 | 19.1841 | 12.2299 | 48.9196 |  | 0.2446 | 0.24272 | 10.3173 | 10.3954
Freq., f = | 2.0342 | Hz. (f >= 1.0) |  | Rigid | 100 | 0.98823 | 19.4674 | 12.4104 | 49.6418 |  | 0.24821 | 0.2464 | 11.7057 | 11.7899
Period, T = | 0.49159 | sec. |  |  | 105 | 1.0021 | 19.7406 | 12.5847 | 50.3386 |  | 0.25169 | 0.24995 | 13.1239 | 13.2139
G = | 0.85 | (Gust Factor, Sect. 6.5.8) |  |  | 110 | 1.0155 | 20.0048 | 12.753 | 51.0122 |  | 0.25506 | 0.25338 | 14.5706 | 14.666
[5 empty] | 120 | 1.0411 | 20.5083 | 13.0741 | 52.2962 |  | 0.52296 | 0.51654 | 33.5859 | 33.9926
[5 empty] | 130 | 1.0652 | 20.9827 | 13.3765 | 53.506 |  | 0.53506 | 0.52901 | 39.6859 | 40.1295
Velocity Pressure (Sect. 6.5.10, Eq. 6-15):
qz = 0.00256*Kz*Kzt*Kd*V^2*I
Net Design Wind Pressures (Sect. 6.5.13):
p = qz*G*Cf (psf)
Net Design Wind Forces (Sect. 6.5.15, Eq. 6-28):
F = qz*G*Cf*D (lb/ft)
Total Shear & Moment @ Base of Vessel:
SV(total) = | 3.8261 | kips
SM(total) = | 159.7367 | ft-kips
Determination of Gust Effect Factor, G: | [10 empty] | SV(total): | SV(total): | SM(total): | SM(total):
[11 empty] | 3.8642 | 3.8261 | 159.7367 | 161.266
Flexible? | No | f >= 1.0 Hz.
1: Simplified Method for Rigid Structure | [11 empty] | Alternate calculation for "f" and "T" for a round, thin-walled cantilevered vessel:
G = | 0.85 | [10 empty] | di = | 3.9375 | = D-(2*t/12), ft.
[12 empty] | I = | 0.76738 | = 0.0491*(D^4-di^4), ft^4
Parameters Used in Both Item #2 and Item #3 Calculations (from Table 6-2): | [11 empty] | m = | 0.0059292 | kip-sec^2/ft^2, m = 0.7854*(D^2-di^2)*γt/g
a^ = | 0.14286 | [10 empty] | f = | 2.0342 | Hz., f = 0.56/h^2*SQRT(E*I/m) (from ASCE 7-05 Ch. C6, Eqn. C6-22a, page 294)
b^ = | 0.84 | [10 empty] | T = | 0.49159 | = 1/f, sec. (fundamental period)
a(bar) = | 0.25
b(bar) = | 0.45 | [10 empty] | Alternate calculation for "f" and "T" for an hexagonal, thin-walled cantilevered vessel:
c = | 0.3 | [10 empty] | di = | 3.9375 | ft., di = D-(2*t/12)
l = | 320 | ft. | [9 empty] | I = | 0.93992 | ft^4, I = 0.06014*(D^4-di^4)
e(bar) = | 0.33333 | [10 empty] | m = | 0.0065377 | kip-sec^2/ft^2, m = 0.8660*(D^2-di^2)*γt/g
z(min) = | 30 | ft. | [9 empty] | f = | 2.144 | Hz., f = 0.56/h^2*SQRT(E*I/m) (from ASCE 7-05 Ch. C6, Eqn. C6-22a, page 294)
[12 empty] | T = | 0.46642 | = 1/f, sec. (fundamental period)
Calculated Parameters Used in Both Rigid and/or Flexible Structure Calculations:
z(bar) = | 48 | = 0.6*h , but not < z(min) , ft. | [9 empty] | Alternate calculation for "f" and "T" for an octagonal, thin-walled cantilevered vessel:
Iz(bar) = | 0.28184 | = c*(33/z(bar))^(1/6) , Eq. 6-5 | [9 empty] | di = | 3.9375 | ft., di = D-(2*t/12)
Lz(bar) = | 362.5705 | = l*(z(bar)/33)^(e(bar)) , Eq. 6-7 | [9 empty] | I = | 0.8971 | ft^4, I = 0.0574*(D^4-di^4)
gq = | 3.4 | (3.4, per Sect. 6.5.8.1) | [9 empty] | m = | 0.006254 | kip-sec^2/ft^2, m = 0.82843*(D^2-di^2)*γt/g
gv = | 3.4 | (3.4, per Sect. 6.5.8.1) | [9 empty] | f = | 2.1416 | Hz., f = 0.56/h^2*SQRT(E*I/m) (from ASCE 7-05 Ch. C6, Eqn. C6-22a, page 294)
gr = | 4.3555 | = (2*(LN(3600*f)))^(1/2)+0.577/(2*LN(3600*f))^(1/2) , Eq. 6-9 | [9 empty] | T = | 0.46695 | = 1/f, sec. (fundamental period)
Q = | 0.89416 | = (1/(1+0.63*((B+h)/Lz(bar))^0.63))^(1/2) , Eq. 6-6
Alternate calculation for "f" and "T" for a square, thin-walled cantilevered vessel:
2: Calculation of G for Rigid Structure | [11 empty] | di = | 3.9375 | ft., di = D-(2*t/12)
G = | 0.86434 | = 0.925*((1+1.7*gq*Iz(bar)*Q)/(1+1.7*gv*Iz(bar))) , Eq. 6-4 | [9 empty] | I = | 1.3024 | ft^4, I = 0.08333*(D^4-di^4)
[12 empty] | m = | 0.0075493 | kip-sec^2/ft^2, m = (D^2-di^2)*γt/g
3: Calculation of Gf for Flexible Structure | [11 empty] | f = | 2.3486 | Hz., f = 0.56/h^2*SQRT(E*I/m) (from ASCE 7-05 Ch. C6, Eqn. C6-22a, page 294)
b = | 0.01 | Damping Ratio | [9 empty] | T = | 0.42579 | = 1/f, sec. (fundamental period)
di = | 3.9375 | = D-(2*t/12), ft. |  | (Inside diameter or clear inside dimension between flats.)
I = | 0.76738 | = 0.0491*(D^4-di^4), ft^4
m = | 0.0059292 | kip-sec^2/ft^2, m = 0.7854*(D^2-di^2)*γt/g
f = | 2.0342 | Hz., f = 0.56/h^2*SQRT(E*I/m) (from ASCE 7-05 Ch. C6, Eqn. C6-22a, page 294)
T = | 0.49159 | = 1/f, sec. (fundamental period)
V(fps) = | N.A. | = V(mph)*(88/60) , ft./sec.
V(bar,zbar) = | N.A. | = b(bar)*(z(bar)/33)^(a(bar))*V*(88/60) , ft./sec. , Eq. 6-14
N1 = | N.A. | = f*Lz(bar)/(V(bar,zbar)) , Eq. 6-12
Rn = | N.A. | = 7.47*N1/(1+10.3*N1)^(5/3) , Eq. 6-11
hh = | N.A. | = 4.6*f*h/(V(bar,zbar))
Rh = | N.A. | = (1/hh)-1/(2*hh^2)*(1-e^(-2*hh)) for hh > 0, or = 1 for hh = 0 , Eq. 6-13a,b
hb = | N.A. | = 4.6*f*D/(V(bar,zbar))
RB = | N.A. | = (1/hb)-1/(2*hb^2)*(1-e^(-2*hb)) for hb > 0, or = 1 for hb = 0 , Eq. 6-13a,b
hd = | N.A. | = 15.4*f*D/(V(bar,zbar))
RL = | N.A. | = (1/hd)-1/(2*hd^2)*(1-e^(-2*hd)) for hd > 0, or = 1 for hd = 0 , Eq. 6-13a,b
R = | N.A. | = ((1/b)*Rn*Rh*RB*(0.53+0.47*RL))^(1/2) , Eq. 6-10
Gf = | N.A. | = 0.925*(1+1.7*Iz(bar)*(gq^2*Q^2+gr^2*R^2)^(1/2))/(1+1.7*gv*Iz(bar)) , Eq. 6-8
Use: G = | 0.85
Note on B9: The Basic Design Wind Speed, V (mph), corresponds to a 3-second gust speed at 33' above ground in Exposure Category "C" and is associated with an annual probability of 0.02 of being equaled or exceeded (50-year mean recurrence interval). For Basic Wind Speed Map (Fig. 6-1) see 'Wind Map' worksheet of this workbook.
Note on B10: TABLE 1-1 Occupancy Category of Buildings and Other Structures for Flood, Wind, Snow, Earthquake, and Ice Loads Nature of Occupancy Occupancy Category Buildings and structures that represent a low hazard to human life in the event of failure including, I but not limited to: - Agriculture facilities - Certain temporary facilities - Minor storage facilities Buildings and other structures except those listed in Categories I, III and IV II Buildings and other structures that represent a substantial hazard to human life in the event of III failure including, but not limited to: - Buildings and other structures where more than 300 people congregate in one area - Buildings and other structures with day-care facilities with capacity greater than 150 - Elementary or secondary school facilities with capacity greater than 250 - Colleges & adult education facilities with a capacity greater than 500 - Health care facilities with a capacity greater than 50 resident patients but not having surgery or emergency treatment facilities - Jails and detention facilities Buildings and other structures, not includes in Occupancy Category IV, with potential to cause substantial economic impact and/or mass disruption of day-to-day civilian life in event of failure, including, but not limited to: - Power generating stations, water treatment facilities, sewage treatment facilities, and telecommunication centers - Buildings and structures not included in Category IV containing sufficient quantities of toxic, explosive, or other hazardous materials dangerous to the public if released Buildings and other structures designated as essential facilities including, but not limited to: IV - Hospitals and health care facilities having surgery or emergency treatment facilities - Fire, rescue and police stations and emergency vehicle garages - Designated earthquake, hurricane or other emergency shelters - Designated emergency preparedness, communication, and operation centers and other facilities required for emergency response - Power-generating stations and other public utility facilities required in an emergency - Ancillary structures required for operation of Category IV structures during an emergency - Aviation control towers, air traffic control centers and emergency aircraft hangars - Water storage facilities and pump structures required to maintain water pressure for fire suppression - Buildings and other structures having critical national defense functions - Buildings and structures containing extremely hazardous materials where quantity of material exceeds a threshold quantity established by authority having jurisdiction
Note on B11: Surface Roughness Categories for the purpose of assigning Exposure Category are defined as follows: Surface Roughness "B": Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single family dwellings or larger. Surface Roughness "C": Open terrain with scattered obstructions having heights generally < 30 ft. This category includes flat open country, grass lands, and all water surfaces in hurricane prone regions. Surface Roughness "D": Flat, unobstructed areas and water surfaces outside hurricane prone regions. This category includes smooth mud flats, salt flats, and unbroken ice. Exposure Categories are defined as follows: Exposure "B": Exposure B shall apply where the ground surface roughness condition, as defined by Surface Roughness B, prevails in the upwind direction for a distance of at least 2600 ft. or 20 times the building height, whichever is greater. Exception: For buildings whose mean roof height <= 30 ft., the upwind distance may be reduced to 1500 ft. Exposure "C": Exposure C shall apply for all cases where exposures B and D do not apply. Exposure "D": Exposure D shall apply where the ground surface roughness, as defined by Surface Roughness D, prevails in the upwind direction for a distance >= 5,000 ft. or 20 times the building height, whichever is greater. Exposure D shall extend into downwind areas of Surface Roughness B or C for a distance of 600 ft. or 20 times the height of the building, whichever is greater.
Note on B12: The Topographic Factor, Kzt, accounts for effect of wind speed-up over isolated hills and escarpments (Sect. 6.5.7 and Fig. 6-4). Kzt = (1=K1*K2*K3)^2 (Eq. 6-3), where: H = height of hill or escarpment relative to the upwind terrain, in feet. Lh = Distance upwind of crest to where the difference in ground elevation is half the height of hill or escarpment, in feet. K1 = factor to account for shape of topographic feature and maximum speed-up effect. K2 = factor to account for reduction in speed-up with distance upwind or downwind of crest. K3 = factor to account for reduction in speed-up with height above local terrain. x = distance (upwind or downwind) from the crest to the building site, in feet. z = height above local ground level, in feet. The effect of wind speed-up shall not be required to be considered (Kzt = 1.0) when H/Lh < 0.2, or H < 15' for Exposures 'C' and 'D', or H < 60' for Exposure 'B'.
Note on B17: Typical tank material unit weights: steel = 490 pcf aluminum = 165 pcf FRP (fiberglass) = 100 - 125 pcf concrete = 145 - 150 pcf
Note on B19: The Damping Ratio, b, is the percent of critical damping. It is only used in the calculation of the Gust Factor, Gf, when a structure is considered "flexible". A structure is considered "flexible" when it has a natural frequency, f < 1 hz. Otherwise the structure is considered "rigid". Suggested range of values is from 0.010 to 0.070. Note: if the structure is "flexible", the smaller the value of the damping ratio, the larger the gust effect factor, Gf, becomes.
Note on B21: Force Coefficients for Chimneys, Tanks, and Similar Structures, Cf (Fig. 6-21): Cf for h/D Values of: Cross-Section Type of Surface 1 7 25 Square (wind normal to face) All 1.3 1.4 2.0 Square (wind along diagonal) All 1.0 1.1 1.5 Hexagonal or Octagonal All 1.0 1.2 1.4 Moderately smooth 0.5 0.6 0.7 Round (D*SQRT(qz)>2.5) Rough (D'/D=0.02) 0.7 0.8 0.9 Very Rough (D'/D=0.08) 0.8 1.0 1.2 Round (D*SQRT(qz)<=2.5) All 0.7 0.8 1.2 D' = depth of protruding elements (ft.) * Note: the original value of 0.2 shown in Figure 6-21 was in error, and the correct value of 1.2 is taken from ASCE 7-05 Code published errata (5-03-07).
Note on B35: If the structure is "rigid", then the minimum of either the calculated value of 'G' for "rigid" structures or 0.85 is used. If the structure is "flexible" then the calculated value of 'G' is used. (See calculations on page 2.)
Note on B49: Total wind shear at base of vessel is calculated using a trapezoidal shaped wind pressure diagram.
Note on B50: Total wind moment at base of vessel is calculated using a trapezoidal shaped wind pressure diagram.
Note on B56: Per ASCE 7-05 Code, structures which have a fundamental (mode 1) natural frequency, f >= 1 Hz are considered "rigid". Per ASCE 7-05 Code, structures which have a fundamental (mode 1) natural frequency, f < 1 Hz are considered "flexible".
Note on B72: The Equivalent Height of the Structure, z(bar). z(bar) = 0.6*h but not less than z(min) from Table C6-6.
Note on B73: The Intensity of Turbulence at height = z(bar). Iz(bar) = c*(33/z(bar))^(1/6)
Note on B74: The Integral Length Scale of Turbulence at the equivalent height. Lz(bar) = l*(z(bar)/33)^(e (bar))
Note on B75: Peak Factor for background response: gq = 3.4 (per Sect. 6.5.8.1)
Note on B76: Peak Factor for wind response: gv = 3.4 (per Sect. 6.5.8.1)
Note on B77: Peak Factor for resonant response: gr = (2*(LN(3600*f)))^(1/2)+0.577/(2*LN(3600*f))^(1/2) Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B78: The Background Response Factor, Q. Q = (1/(1+0.63*((B+h)/Lz(bar))^0.63))^(1/2) where: B = structure width normal to wind h = structure mean roof height
Note on B81: The Gust Effect Factor, G, for a "rigid" structure. G = 0.925*((1+1.7*gq*Iz(bar)*Q)/(1+1.7*gv*Iz(bar))) where: gq = 3.4 and gv = 3.4
Note on B90: The Basic Wind Speed, V, converted from units of mph to ft/sec. V(fps) = V(mph)*(88/60)
Note on B91: The Mean Hourly Wind Speed, V(bar,zbar). V(bar,zbar) = b(bar)*(z(bar)/33)^(a(bar))*V*(88/60)
Note on B92: N1 = f*Lz(bar)/(V(bar,zbar)) Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B93: Rn = 7.47*N1/(1+10.3*N1)^(5/3)
Note on B94: hh = 4.6*f*h/(V(bar,zbar)) Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B95: Rh = (1/hh)-1/(2*hh^2)*(1-e^(-2*hh)) for hh > 0 or: Rh = 1 for hh = 0
Note on B96: hb =4.6*f*D/(V(bar,zbar)) where: D = vessel width normal to wind Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B97: RB = (1/hB)-1/(2*hB^2)*(1-e^(-2*hB)) for hB > 0 or: RB = 1 for hB = 0
Note on B98: hd = 15.4*f*D/(V(bar,zbar)) where: D = depth of vessel parallel to wind Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B99: RL = (1/hL)-1/(2*hL^2)*(1-e^(-2*hL)) for hL > 0 or: RL = 1 for hL = 0
Note on B100: The Resonant Response Factor, R. R = ((1/b)*Rn*Rh*Rb*(0.53+0.47*Rd))^1/2
Note on B101: The Gust Effect Factor, Gf, for a "flexible" building. Gf = 0.925*(1+1.7*Iz(bar)*(gq^2*Q^2+gr^2*R^2)^(1/2))/(1+1.7*gv*Iz(bar))
Note on B102: For a rigid structure, the smaller of the value of either 0.85 or the value as calculated in item #2 is used for the gust effect factor, G.
Note on C29: Terrain Exposure Constants (Table 6-2) Exposure Category a zg (ft) B 7.0 1,200 C 9.5 900 D 11.5 700
Note on C30: Terrain Exposure Constants (Table 6-2) Exposure Category a zg (ft) B 7.0 1,200 C 9.5 900 D 11.5 700
Note on C31: Importance Factor, I (Table 6-1): Non-Hurricane Prone Regions Hurricane Prone Regions Category and Hurricane Prone Regions with V > 100 mph with V = 85-100 mph and Alaska I 0.87 0.77 II 1.00 1.00 III 1.15 1.15 IV 1.15 1.15 Note: in the U.S. and its territories hurricane prone regions are defined as: 1. U.S. Atlantic Ocean and Gulf of Mexico coasts where the basic wind speed is > 90 mph. 2. Hawaii, Puerto Rico, Guam, Virgin Islands, and American Samoa.
Note on C80: The Gust Effect Factor, G, for a rigid structure as calculated from Eqn. 6-4.
Note on D41: Per Code Section 6.1.4.1, the minimum wind load to be used shall not be less than 10 psf.
Note on D58: The Gust Effect Factor, G, for rigid structures may be simply taken as 0.85 for all structure exposure conditions.
Note on D83: The Gust Effect Factor, Gf, for a flexible structure as calculated from Eqn 6-8. Note: calculations below are applicable only for "flexible" structures which have a natural frequency, f < 1 hz.
Note on H61: Terrain Exposure Constants (Table 6-2) Exposure a zg(ft) a^ b^ a(bar) b(bar) c l(ft) e z(min) B 7.0 1200 1/7 0.84 1/4.0 0.45 0.30 320 1/3.0 30 C 9.5 900 1/9.5 1.00 1/6.5 0.65 0.20 500 1/5.0 15 D 11.5 700 1/11.5 1.07 1/9.0 0.80 0.15 650 1/8.0 7 Note: z(min) = minimum height used to ensure that the equivalent height z(bar) is greater of 0.6*h or z(min). For buildings with h<= z(min), z(bar) shall be taken as z(min).
Note on J3: Note: This program assumes structures are a maximum of 600 feet tall.
Note on AA1: "ASCE705W.xls" written by: Alex Tomanovich, P.E.
Note on AC19: Note: value of wind velocity pressure (qz) determined at lowest level is used in the evaluation of this expression.
Note on AC20: If applicable, then user may take the value of 'Cf' from this cell, interpolated from Figure 6-21 above, and input it into cell B21.
Note on AH11: Note: the original value of 0.2 shown in Figure 6-21 was in error, and the correct value of 1.2 is taken from ASCE 7-05 Code published errata (5-03-07).
Ground
D
h
Hb >= 0
Wind

## Open Structures (no roof)
WIND LOADING ANALYSIS - Open Structures without Roofs | [9 empty] | CALCULATIONS: |  |  | Version 1.4
Per ASCE 7-05 Code
Using Method 2: Analytical Procedure (Section 6.5) for Other Structures of Any Height | [8 empty] | I | Determine a, zg, I:
Job Name: |  |  |  |  | Subject: |  |  |  | II | a = | 9.5 | (Table 6-2)
Job Number: |  |  |  |  | Originator: |  |  | Checker: | III | zg = | 900 | (Table 6-2)
[9 empty] | IV | I = | 1.15 | (Table 6-1) |  | Note: this worksheet DOES NOT address
Input Data: | [8 empty] | B |  |  |  |  | open structures with roofs!
[5 empty] | Resulting Parameters and Coefficients: |  |  |  | C
| Wind Speed, V = | 90 | mph | [5 empty] | D
| Class., Occ. Category = | III | (Table 1-1) |  | If z < 15 then: Kz = 2.01*(15/zg)^(2/a) |  |  |  | Y
| Exposure Category = | C | (Sect. 6.5.6) |  | If z >= 15 then: Kz = 2.01*(z/zg)^(2/a) |  |  |  | N
| Topo. Factor, Kzt = | 1 | (Sect. 6.5.7) |  | a = | 9.5 | (Table 6-2)
| Height of Structure, h = | 8.5 | ft. |  | zg = | 900 | (Table 6-2)
| Structure Width, B = | 3 | ft. (normal to wind) |  | I = | 1.15 | (Table 6-1)
| Structure Length, L = | 7,5 | ft. (parallel to wind) |  | freq., f = | 10.044 | Hz. (f >=1) | Rigid
| Damping Ratio, b = | 0.01 | (0.010 to 0.070) |  | G = | 0.85 | (Gust Factor, Sect. 6.5.8)
| Period Coefficient, Ct = | 0.02 | (0.020 to 0.035)
| Direct. Factor, Kd = | 0.85 | (Table 6-4) |  | Velocity Pressure (Sect. 6.5.10, Eq. 6-15):
| Hurricane Region? | N |  |  | qz = 0.00256*Kz*Kzt*Kd*V^2*I
Net Design Wind Pressures (Sect. 6.5.15):
Note: Per Code Section 6.1.4.1, design wind force for open |  |  |  |  | p = qz*G*Cf (psf), where 'qz' is evaluated at
buildings and other structures shall not be less than 10 psf |  |  |  |  | height 'z' of the centroid of projected area. | [8 empty] | Note: User is to input applicable
multiplied by the area, 'Af', the area normal to wind direction. | [13 empty] | values of Cf in table at left.
Use force coefficients, Cf,
| Open Structure - Net Design Wind Pressures, p | [12 empty] | from Figures 6-22 and 6-23.
Force Coefficient, Cf
| z | Kz | qz | qz*G | 1.2 | 1.6 | 1.8 | 2 | [5 empty] | User Input for Height, z (ft.):
| (ft.) |  | (psf) | (psf) | p | p | p | p | [5 empty] | N | Use Input Values?
[5 empty] | (psf) | (psf) | (psf) | (psf)
| 0 | 0.84888 | 17.2064 | 14.6254 | 17.5505 | 23.4007 | 26.3258 | 29.2509
For z = h: | 8.5 | 0.84888 | 17.2064 | 14.6254 | 17.5505 | 23.4007 | 26.3258 | 29.2509
Determination of Gust Effect Factor, G:
Flexible? | No | f >=1 Hz.
1: Simplified Method for Rigid Structure
G = | 0.85
Parameters Used in Both Item #2 and Item #3 Calculations (from Table 6-2):
a^ = | 0.10526
b^ = | 1
a(bar) = | 0.15385
b(bar) = | 0.65
c = | 0.2
l = | 500 | ft.
e(bar) = | 0.2
z(min) = | 15 | ft.
Calculated Parameters Used in Both Rigid and/or Flexible Structure Calculations:
z(bar) = | 15 | = 0.6*h , but not < z(min) , ft.
Iz(bar) = | 0.22809 | = c*(33/z(bar))^(1/6) , Eq. 6-5
Lz(bar) = | 427.0566 | = l*(z(bar)/33)^(e(bar)) , Eq. 6-7
gq = | 3.4 | (3.4, per Sect. 6.5.8.1)
gv = | 3.4 | (3.4, per Sect. 6.5.8.1)
gr = | 4.7076 | = (2*(LN(3600*f)))^(1/2)+0.577/(2*LN(3600*f))^(1/2) , Eq. 6-9
Q = | 0.96918 | = (1/(1+0.63*((B+h)/Lz(bar))^0.63))^(1/2) , Eq. 6-6
2: Calculation of G for Rigid Structure
G = | 0.90879 | = 0.925*((1+1.7*gq*Iz(bar)*Q)/(1+1.7*gv*Iz(bar))) , Eq. 6-4
3: Calculation of Gf for Flexible Structure
b = | 0.01 | Damping Ratio
Ct = | 0.02 | Period Coefficient
T = | 0.099562 | = Ct*h^(3/4) , sec. (Period)
f = | 10.044 | = 1/T , Hz. (Natural Frequency)
V(fps) = | N.A. | = V(mph)*(88/60) , ft./sec.
V(bar,zbar) = | N.A. | = b(bar)*(z(bar)/33)^(a(bar))*V*(88/60) , ft./sec. , Eq. 6-14
N1 = | N.A. | = f*Lz(bar)/(V(bar,zbar)) , Eq. 6-12
Rn = | N.A. | = 7.47*N1/(1+10.3*N1)^(5/3) , Eq. 6-11
hh = | N.A. | = 4.6*f*h/(V(bar,zbar))
Rh = | N.A. | = (1/hh)-1/(2*hh^2)*(1-e^(-2*hh)) for hh > 0, or = 1 for hh = 0 , Eq. 6-13a,b
hb = | N.A. | = 4.6*f*B/(V(bar,zbar))
RB = | N.A. | = (1/hb)-1/(2*hb^2)*(1-e^(-2*hb)) for hb > 0, or = 1 for hb = 0 , Eq. 6-13a,b
hd = | N.A. | = 15.4*f*L/(V(bar,zbar))
RL = | N.A. | = (1/hd)-1/(2*hd^2)*(1-e^(-2*hd)) for hd > 0, or = 1 for hd = 0 , Eq. 6-13a,b
R = | N.A. | = ((1/b)*Rn*Rh*RB*(0.53+0.47*RL))^(1/2) , Eq. 6-10
Gf = | N.A. | = 0.925*(1+1.7*Iz(bar)*(gq^2*Q^2+gr^2*R^2)^(1/2))/(1+1.7*gv*Iz(bar)) , Eq. 6-8
Use: G = | 0.85
| Other Structures - Method 2 |  |  |  | All Heights
| Figure 6-22 |  | Force Coefficients |  | Open Signs & | [8 empty] | For Flat Sided Members from Figure 6-22:
|  |  | Cf |  | Lattice Frameworks | [8 empty] | Solid Area = | 6250 | ft.^2
| e |  | Flat-Sided |  | Rounded Members | [8 empty] | Gross Area = | 12500 | ft.^2
|  |  | Members |  | D*SQRT(qz) <= 2.5 |  | D*SQRT(qz) > 2.5 | [6 empty] | Solidity Ratio, e = | 0.5 |  | e = Solid Area/Gross Area
[14 empty] | Cf = | 1.6 |  | Cf from Figure 6-22
| < 0.1 |  | 2 |  | 1.2 |  | 0.8
For Rounded Members from Figure 6-22:
[14 empty] | D = | 10 | ft.
| 0.1 to 0.29 |  | 1.8 |  | 1.3 |  | 0.9 | [6 empty] | qz = | 25 | psf
[14 empty] | Solid Area = | 6250 | ft.^2
[14 empty] | Gross Area = | 12500 | ft.^2
| 0.3 to 0.7 |  | 1.6 |  | 1.5 |  | 1.1 | [6 empty] | Solidity Ratio, e = | 0.5 |  | e = Solid Area/Gross Area
[14 empty] | D*SQRT(qz) = | 50
[14 empty] | Cf = | N.A. |  | Cf for D*SQRT(qz) <= 2.5
Notes: | 1. Signs with openings comprising 30% or more of the gross area are classified as open signs. | [12 empty] | Cf = | 1.1 |  | Cf for D*SQRT(qz) > 2.5
| 2. The calculation of the design wind forces shall be based on the area of all exposed members | [12 empty] | Use: Cf = | 1.1 |  | Cf from Figure 6-22
and elements projected on a plane normal to the wind direction. Forces shall be assumed to
act parallel to the wind direction.
3. The area 'Af' consistent with these force coefficients is the solid area projected normal to the
wind direction.
4. Notation:
e = ratio of solid area to gross area
D = diameter of a typical round member, in feet.
qz = velocity pressure evaluated at height 'z' above ground in psf.
| Other Structures - Method 2 |  |  |  | All Heights
| Figure 6-23 |  | Force Coefficients
|  |  | Cf |  | Trussed Towers
Open Structures
| Tower Cross Section |  |  |  | Cf | [8 empty] | For Trussed Towers from Figure 6-23:
[14 empty] | Solid Area = | 6250 | ft.^2
[14 empty] | Gross Area = | 12500 | ft.^2
| Square |  |  |  | 4.0*e^2 - 5.9*e + 4.0 | [8 empty] | Solidity Ratio, e = | 0.5 |  | e = Solid Area/Gross Area
[14 empty] | Square Tower Cf = | 2.05 |  | Cf = 4.0*e^2 - 5.9*e + 4.0
[14 empty] | Triangle Tower Cf = | 1.9 |  | Cf = 3.4*e^2 - 4.7*e + 3.4
| Triangle |  |  |  | 3.4*e^2 - 4.7*e + 3.4
Notes: | 1. For all wind directions considered, area 'Af' consistent with force coefficients shall be solid area
of tower face projected on plane of that face for tower segment under consideration.
2. Specified force coefficients are for towers with structural angles or similar flat-sided members.
3. For towers containing rounded member, it is acceptable to multiply specified force coefficients
by following factor when determining wind forces on such members: 0.51*e^2 + 0.57 <= 1.0.
4. Wind forces shall be applied in directions resulting in maximum member forces and reactions.
For towers with square cross-sections, wind forces shall be multiplied by following factor when
wind is directed along a tower diagonal: 1+ 0.75*e <= 1.2.
5. Wind forces on tower appurtenances such as ladder, conduits, lights, elevators, etc., shall be
calculated using appropriate force coefficients for these elements.
6. Notation: e = ratio of solid area to gross area of one tower face for segment considered.
Note on B60: Structures which have a natural frequency, f >= 1 Hz are considered "rigid". Structures which have a natural frequency, f < 1 Hz are considered "flexible".
Note on B76: The Equivalent Height of the Structure, z(bar). z(bar) = 0.6*h but not less than z(min) from Table C6-6.
Note on B77: The Intensity of Turbulence at height = z(bar). Iz(bar) = c*(33/z(bar))^(1/6)
Note on B78: The Integral Length Scale of Turbulence at the equivalent height. Lz(bar) = l*(z(bar)/33)^(e (bar))
Note on B79: Peak Factor for background response: gq = 3.4 (per Sect. 6.5.8.1)
Note on B80: Peak Factor for wind response: gv = 3.4 (per Sect. 6.5.8.1)
Note on B81: Peak Factor for resonant response: gr = (2*(LN(3600*f)))^(1/2)+0.577/(2*LN(3600*f))^(1/2) Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B82: The Background Response Factor, Q. Q = (1/(1+0.63*((B+h)/Lz(bar))^0.63))^(1/2) where: B = structure width normal to wind h = structure mean roof height
Note on B85: The Gust Effect Factor, G, for a "rigid" structure. G = 0.925*((1+1.7*gq*Iz(bar)*Q)/(1+1.7*gv*Iz(bar))) where: gq = 3.4 and gv = 3.4
Note on B92: The Basic Wind Speed, V, converted from units of mph to ft/sec. V(fps) = V(mph)*(88/60)
Note on B93: The Mean Hourly Wind Speed, V(bar,zbar). V(bar,zbar) = b(bar)*(z(bar)/33)^(a(bar))*V*(88/60)
Note on B94: N1 = f*Lz(bar)/(V(bar,zbar)) Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B95: Rn = 7.47*N1/(1+10.3*N1)^(5/3)
Note on B96: hh = 4.6*f*h/(V(bar,zbar)) Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B97: Rh = (1/hh)-1/(2*hh^2)*(1-e^(-2*hh)) for hh > 0 or: Rh = 1 for hh = 0
Note on B98: hb =4.6*f*B/(V(bar,zbar)) where: B = building width normal to wind Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B99: RB = (1/hB)-1/(2*hB^2)*(1-e^(-2*hB)) for hB > 0 or: RB = 1 for hB = 0
Note on B100: hd = 15.4*f*L/(V(bar,zbar)) where: L = depth of building parallel to wind Note: the symbol, f, was substituted for the original symbol, n1, in the equation above.
Note on B101: RL = (1/hL)-1/(2*hL^2)*(1-e^(-2*hL)) for hL > 0 or: RL = 1 for hL = 0
Note on B102: The Resonant Response Factor, R. R = ((1/b)*Rn*Rh*Rb*(0.53+0.47*Rd))^1/2
Note on B103: The Gust Effect Factor, Gf, for a "flexible" building. Gf = 0.925*(1+1.7*Iz(bar)*(gq^2*Q^2+gr^2*R^2)^(1/2))/(1+1.7*gv*Iz(bar))
Note on B104: For a rigid structure, the smaller of the value of either 0.85 or the value as calculated in item #2 is used for the gust effect factor, G.
Note on C9: The Basic Design Wind Speed, V (mph), corresponds to a 3-second gust speed at 33' above ground in Exposure Category "C" and is associated with an annual probability of 0.02 of being equaled or exceeded (50-year mean recurrence interval). For Basic Wind Speed Map (Fig. 6-1) see 'Wind Map' worksheet of this workbook.
Note on C10: TABLE 1-1 Occupancy Category of Buildings and Other Structures for Flood, Wind, Snow, Earthquake, and Ice Loads Nature of Occupancy Occupancy Category Buildings and structures that represent a low hazard to human life in the event of failure including, I but not limited to: - Agriculture facilities - Certain temporary facilities - Minor storage facilities Buildings and other structures except those listed in Categories I, III and IV II Buildings and other structures that represent a substantial hazard to human life in the event of III failure including, but not limited to: - Buildings and other structures where more than 300 people congregate in one area - Buildings and other structures with day-care facilities with capacity greater than 150 - Elementary or secondary school facilities with capacity greater than 250 - Colleges & adult education facilities with a capacity greater than 500 - Health care facilities with a capacity greater than 50 resident patients but not having surgery or emergency treatment facilities - Jails and detention facilities Buildings and other structures, not includes in Occupancy Category IV, with potential to cause substantial economic impact and/or mass disruption of day-to-day civilian life in event of failure, including, but not limited to: - Power generating stations, water treatment facilities, sewage treatment facilities, and telecommunication centers - Buildings and structures not included in Category IV containing sufficient quantities of toxic, explosive, or other hazardous materials dangerous to the public if released Buildings and other structures designated as essential facilities including, but not limited to: IV - Hospitals and health care facilities having surgery or emergency treatment facilities - Fire, rescue and police stations and emergency vehicle garages - Designated earthquake, hurricane or other emergency shelters - Designated emergency preparedness, communication, and operation centers and other facilities required for emergency response - Power-generating stations and other public utility facilities required in an emergency - Ancillary structures required for operation of Category IV structures during an emergency - Aviation control towers, air traffic control centers and emergency aircraft hangars - Water storage facilities and pump structures required to maintain water pressure for fire suppression - Buildings and other structures having critical national defense functions - Buildings and structures containing extremely hazardous materials where quantity of material exceeds a threshold quantity established by authority having jurisdiction
Note on C11: Surface Roughness Categories for the purpose of assigning Exposure Category are defined as follows: Surface Roughness "B": Urban and suburban areas, wooded areas or other terrain with numerous closely spaced obstructions having the size of single family dwellings or larger. Surface Roughness "C": Open terrain with scattered obstructions having heights generally < 30 ft. This category includes flat open country, grass lands, and all water surfaces in hurricane prone regions. Surface Roughness "D": Flat, unobstructed areas and water surfaces outside hurricane prone regions. This category includes smooth mud flats, salt flats, and unbroken ice. Exposure Categories are defined as follows: Exposure "B": Exposure B shall apply where the ground surface roughness condition, as defined by Surface Roughness B, prevails in the upwind direction for a distance of at least 2600 ft. or 20 times the building height, whichever is greater. Exception: For buildings whose mean roof height <= 30 ft., the upwind distance may be reduced to 1500 ft. Exposure "C": Exposure C shall apply for all cases where exposures B and D do not apply. Exposure "D": Exposure D shall apply where the ground surface roughness, as defined by Surface Roughness D, prevails in the upwind direction for a distance >= 5,000 ft. or 20 times the building height, whichever is greater. Exposure D shall extend into downwind areas of Surface Roughness B or C for a distance of 600 ft. or 20 times the height of the building, whichever is greater.
Note on C12: The Topographic Factor, Kzt, accounts for effect of wind speed-up over isolated hills and escarpments (Sect. 6.5.7 and Fig. 6-4). Kzt = (1+K1*K2*K3)^2 (Eq. 6-3), where: H = height of hill or escarpment relative to the upwind terrain, in feet. Lh = Distance upwind of crest to where the difference in ground elevation is half the height of hill or escarpment, in feet. K1 = factor to account for shape of topographic feature and maximum speed-up effect. K2 = factor to account for reduction in speed-up with distance upwind or downwind of crest. K3 = factor to account for reduction in speed-up with height above local terrain. x = distance (upwind or downwind) from the crest to the building site, in feet. z = height above local ground level, in feet. The effect of wind speed-up shall not be required to be considered (Kzt = 1.0) when H/Lh < 0.2, or H < 15' for Exposures 'C' and 'D', or H < 60' for Exposure 'B'.
Note on C16: The Damping Ratio, b, is the percent of critical damping. It is only used in the calculation of the Gust Factor, Gf, when a structure is considered "flexible". A structure is considered "flexible" when it has a natural frequency, f < 1 hz. Otherwise the structure is considered "rigid". Suggested range of values is from 0.010 to 0.070. Note: if the structure is "flexible", the smaller the value of the damping ratio, the larger the gust effect factor, Gf, becomes.
Note on C17: The structure Period Coefficient, Ct, has suggested range of values from 0.020 to 0.035. It is used in the equation for the assumed period of the structure: T = Ct*h^3/4. Then the natural frequency, f, is determined by: f = 1/T. It is only used in the calculation of the Gust Factor, Gf, when a structure is considered "flexible". A structure is considered "flexible" when it has a natural frequency, f < 1 hz. Otherwise the structure is considered "rigid". Note: if the period, T, or the natural frequency, f, is already known (obtained by other means), then the value of Ct may be "manipulated" to give the desired results for T and f.
Note on C18: Wind Directionality Factor, Kd (Table 6-4) Structure Type Kd Buildings Main Wind-Force Resisting System 0.85 Components and Cladding 0.85 Note: this factor shall only be applied when used in conjunction with load combinations specified in Sect. 2.3 and 2.4. Otherwise, use Kd = 1.0.
Note on C84: The Gust Effect Factor, G, for a rigid structure as calculated from Eqn. 6-4.
Note on D62: The Gust Effect Factor, G, for rigid structures may be simply taken as 0.85 for all structure exposure conditions.
Note on D87: The Gust Effect Factor, Gf, for a flexible structure as calculated from Eqn 6-8. Note: calculations below are applicable only for "flexible" structures which have a natural frequency, f < 1 hz.
Note on G16: If the structure is "rigid", then the minimum of either the calculated value of 'G' for "rigid" structures or 0.85 is used. If the structure is "flexible" then the calculated value of 'G' is used. (See calculations on page 2.)
Note on H12: Terrain Exposure Constants (Table 6-2) Exposure Category a zg (ft) B 7.0 1,200 C 9.5 900 D 11.5 700
Note on H13: Terrain Exposure Constants (Table 6-2) Exposure Category a zg (ft) B 7.0 1,200 C 9.5 900 D 11.5 700
Note on H14: Importance Factor, I (Table 6-1): Non-Hurricane Prone Regions Hurricane Prone Regions Category and Hurricane Prone Regions with V > 100 mph with V = 85-100 mph and Alaska I 0.87 0.77 II 1.00 1.00 III 1.15 1.15 IV 1.15 1.15 Note: in the U.S. and its territories hurricane prone regions are defined as: 1. U.S. Atlantic Ocean and Gulf of Mexico coasts where the basic wind speed is > 90 mph. 2. Hawaii, Puerto Rico, Guam, Virgin Islands, and American Samoa.
Note on H65: Terrain Exposure Constants (Table 6-2) Exposure a zg(ft) a^ b^ a(bar) b(bar) c l(ft) e z(min) B 7.0 1200 1/7 0.84 1/4.0 0.45 0.30 320 1/3.0 30 C 9.5 900 1/9.5 1.00 1/6.5 0.65 0.20 500 1/5.0 15 D 11.5 700 1/11.5 1.07 1/9.0 0.80 0.15 650 1/8.0 7 Note: z(min) = minimum height used to ensure that the equivalent height z(bar) is greater of 0.6*h or z(min). For buildings with h<= z(min), z(bar) shall be taken as z(min).
Note on I20: Per Code Section 6.1.4.1, the design wind force for open buildings and other structures shall not be less than 10 psf multiplied by the area, 'Af', the area normal to the wind direction.
Note on I25: Per Code Section 6.1.4.1, the design wind force for open buildings and other structures shall not be less than 10 psf multiplied by the area, 'Af', the area normal to the wind direction.
Note on I26: Note: User is to input applicable values of the force coefficient, 'Cf', in the table. (Four different values are permitted.) See page 3 below for details and replication of ASCE 7-05 Figures 6-22 and 6-23.
Note on J3: Note: This program assumes open structures are a maximum of 500 ft. tall.
Note on AA1: "ASCE705W.xls" written by: Alex Tomanovich, P.E.

## Wind Map
FIGURE 6-1: Basic Wind Speed
FIGURE 6-1a: Western Gulf of Mexico Hurricane Coastline
FIGURE 6-1b: Eastern Gulf & Southeastern U.S. Hurricane Coastline
FIGURE 6-1c: Mid and Northern Atlantic Hurricane Coastline